## 工作表1
SIGNAL_NAME | DESC | SIG_TYPE | SIG_LEVEL | PWR_SRC | 2_HI_ALARM | 1_HI_ALARM | 1_LO_ALARM | 2_LO_ALARM | ALARM_UNITS | SOE | HIST | DEVICE_LO | DEVICE_HI | DEVICE_UNITS | DISPLAY_LO | DISPLAY_HI | DISPLAY_UNITS | UNIT AREA | EER LOCATION | PID | SENSOR TYPE | FROM | TO | DEADBAND | PERIODIC LOG | POST TRIP REVIEW | REMARK
=C10QCG01BQ301XB48 | U1 NH3 UNLOADING COMP AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCG01BQ301XQ01 | U1 NH3 UNLOADING COMP AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCG01BQ302XQ01 | U1 NH3 STG TK AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCG01BQ303XQ01 | U1 NH3 STG TK AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCG01BQ304XQ01 | U1 NH3 ACC AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCG01BQ305XQ01 | U1 NH3 VAP AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCG01XD301XB96 | U1 NH3 LOC ALM CMN EMRG | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | LCP | DCDAS | - | - | -
=C10QCG11BL001XG01 | U1 NH3 UNLOAD COMP LIQ TRAP LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | Float Level Switch | FIELD | DCDAS | - | - | -
=C10QCG11BL001XH11 | U1 NH3 UNLOAD COMP LIQ TRAP LSH LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCG11BP002XG01 | U1 NH3 UNLOAD COMP PDS H | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | D/P Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCG11BP002XH11 | U1 NH3 UNLOAD COMP PDS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCG11BP003XG52 | U1 NH3 UNLOAD COMP SUCTION PS L | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCG11BP003XH62 | U1 NH3 UNLOAD COMP SUCTION PS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCG11BP004XG01 | U1 NH3 UNLOAD COMP PS H | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCG11BP004XH11 | U1 NH3 UNLOAD COMP PS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCG11BT001XG01 | U1 NH3 UNLOAD COMP TS H | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | Temperature Switch | FIELD | DCDAS | - | - | -
=C10QCG11BT001XH11 | U1 NH3 UNLOAD COMP TS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCG11GQ001XB01 | U1 NH3 UNLOAD COMP ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | MCC | DCDAS | - | - | -
=C10QCG11GQ001XB20 | U1 NH3 UNLOAD COMP LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | LCP | DCDAS | - | - | -
=C10QCG11GQ001XB41 | U1 NH3 UNLOAD COMP LOC START CMD | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | LCP | DCDAS | - | - | -
=C10QCG11GQ001XB42 | U1 NH3 UNLOAD COMP LOC STOP CMD | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | LCP | DCDAS | - | - | -
=C10QCG11GQ001XB49 | U1 NH3 UNLOAD COMP ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | MCC | DCDAS | - | - | -
=C10QCG11GQ001XB50 | U1 NH3 UNLOAD COMP PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | MCC | DCDAS | - | - | -
=C10QCG11GQ001XB55 | U1 NH3 UNLOAD COMP FAULT LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCG11GQ001XB61 | U1 UNLOAD COMP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | DCDAS | MCC | - | - | -
=C10QCG11GQ001XB62 | U1 NH3 UNLOAD COMP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | DCDAS | MCC | - | - | -
=C10QCG11GQ001XB63 | U1 NH3 UNLOAD COMP START LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCG11GQ001XB64 | U1 NH3 UNLOAD COMP STOP LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCG11GQ001XB69 | U1 NH3 UNLOAD COMP STOP LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | DCDAS | MCC | - | - | -
=C10QCG11GQ001XB78 | U1 NH3 UNLOAD COMP REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | - | MCC | DCDAS | - | - | -
=C10QCM01BP001XG01 | U1 NH3 UNLOAD COMP PSV VENT PS H | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCV11BP001XG52 | U1 NH3 UNLOAD COMP OIL PS L | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCV11BP001XH62 | U1 NH3 UNLOAD COMP OIL PS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C10XLA01QM062XB62 | U1 NH3 UNLOAD COMPR SPY XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10XLA01QM062XG01 | U1 NH3 UNLOAD COMP SPY XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM062XG02 | U1 NH3 UNLOAD COMP SPY XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM062XG33 | U1 NH3 UNLOAD COMP SPY XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C10XLA01QM062XG34 | U1 NH3 UNLOAD COMP SPY XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6001 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C10QCG01BP302XQ01 | FR U1 NH3 STG TK TO U1 NH3 ACC PIT | D-AI | 4-20mA | S | - | 0.6 | 0.38 | - | MPaG | NO | YES | - | - | - | 0 | 1.112 | MPaG | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCG01BQ302XB48 | U1 NH3 STG TK AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCG01BQ303XB48 | U1 NH3 STG TK AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCL01BF301XB27 | TO U1 NH3 STG TK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 30 | m3/hr | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C10QCL01BF301XQ01 | TO U1 NH3 STG TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 30 | m3/hr | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C10QCL01BF301XQ23 | TO U1 NH3 STG TK LOC IND | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 30 | m3/hr | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Local Indicator | DCDAS | LCP | - | - | -
=C10QCL01BL001XG01 | U1 NH3 STG TK LIS HIGH | D-DI | 24VDC | S | - | 2650 | - | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10QCL01BL001XG52 | U1 NH3 STG TK LIS L | D-DI | 24VDC | S | - | - | 320 | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10QCL01BL001XH11 | U1 NH3 STG TK LIS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCL01BL001XH62 | U1 NH3 STG TK LIS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCL01BL301XQ01 | U1 NH3 STG TK LIT | D-AI | 4-20mA | S | - | 2650 | 320 | - | mm | NO | YES | - | - | - | 200 | 3200 | mm | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Radar Level Transmitter | FIELD | DCDAS | - | - | -
=C10QCL01BL301XQ23 | U1 NH3 STG TK LIT LOC IND | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 200 | 3200 | mm | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Local Indicator | DCDAS | FIELD | - | - | -
=C10QCL01BP001XG01 | U1 NH3 STG TK PS H | D-DI | 24VDC | S | - | 1.28 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCL01BP001XG52 | U1 NH3 STG TK PS L | D-DI | 24VDC | S | - | - | 0.82 | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCL01BP001XH11 | U1 NH3 STG TK PS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCL01BP001XH62 | U1 NH3 STG TK PS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCL01BP301XQ01 | U1 NH3 STG TK PIT | D-AI | 4-20mA | S | 1.64 | 1.28 | 0.82 | 0.55 | MPaG | NO | YES | - | - | - | 0 | 2.284 | MPaG | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCL01BT301XH11 | U1 NH3 STG TK TS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCL01BT301XH62 | U1 NH3 STG TK TS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCL01BT301XQ01 | U1 NH3 STG TK TIT | D-AI | 4-20mA | S | - | 42 | 22 | - | ℃ | NO | YES | - | - | - | -50 | 100 | ℃ | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C10QCL01QM061XB61 | FR U1 NH3 LORRY TO U1 NH3 STG TK XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C10QCL01QM061XG01 | FR U1 NH3 LORRY TO U1 NH3 STG TK XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCL01QM061XG02 | FR U1 NH3 LORRY TO U1 NH3 STG TK XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCL01QM061XG33 | FR U1 NH3 LORRY TO U1 NH3 STG TK XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C10QCL01QM061XG34 | FR U1 NH3 LORRY TO U1 NH3 STG TK XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C10QCL01QM081XB01 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCL01QM081XB02 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCL01QM081XB20 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCL01QM081XB49 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | MCC | DCDAS | - | - | -
=C10QCL01QM081XB50 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | MCC | DCDAS | - | - | -
=C10QCL01QM081XB61 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | MCC | - | - | -
=C10QCL01QM081XB62 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | MCC | - | - | -
=C10QCL01QM081XB63 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C10QCL01QM081XB64 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C10QCL01QM081XB87 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCL01QM081XB88 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCL01QM081XG33 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCL01QM081XG34 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCL01QM081XG35 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C10QCL01QM081XG36 | FR U1 NH3 STG TK TO U1 NH3 VAP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C10QCL01XD301XB95 | U1 NH3 STG TK LCP LAMP TEST | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | - | LCP | DCDAS | - | - | -
=C10QCM01BP002XG01 | U1 NH3 LORRY PSV VENT PS H | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCM01BP003XG01 | U1 NH3 STG TK PSV VENT PS H | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10XLA01QM061XB62 | U1 NH3 STG TK SPY XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10XLA01QM061XG01 | U1 NH3 STG TK SPY XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM061XG02 | U1 NH3 STG TK SPY XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM061XG33 | U1 NH3 STG TK SPY XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C10XLA01QM061XG34 | U1 NH3 STG TK SPY XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6002 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C10QCG01BP001XG01 | U1 NH3 ACC PSH | D-DI | 24VDC | S | - | 0.6 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCG01BP301XQ01 | FR U1 NH3 VAP TO U1 NH3 STG TK PIT | D-AI | 4-20mA | S | - | 1.28 | 0.82 | - | MPaG | NO | YES | - | - | - | 0 | 2.284 | MPaG | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCG01BP303XQ01 | FR NH3 ACC TO U1 HRSG NH3 MIXER PIT | D-AI | 4-20mA | S | - | 0.6 | 0.38 | - | MPaG | NO | YES | - | - | - | 0 | 1.112 | MPaG | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCG01BQ304XB48 | U1 NH3 ACC AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCG01BQ305XB48 | U1 NH3 VAP AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C10QCG01BT301XQ01 | FR U1 NH3 VAP TO U1 NH3 STG TK TIT | D-AI | 4-20mA | S | - | 42 | 22 | - | ℃ | NO | YES | - | - | - | -50 | 100 | ℃ | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C10QCG01BT302XQ01 | U1 NH3 VAP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | Temperature Transmitter | LCP | DCDAS | - | - | -
=C10QCG01EB001XB01 | U1 NH3 VAP RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | - | LCP | DCDAS | - | - | -
=C10QCG01EB001XB20 | U1 NH3 VAP LOC STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | - | LCP | DCDAS | - | - | -
=C10QCG01EB001XB40 | U1 NH3 VAP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | - | LCP | DCDAS | - | - | -
=C10QCG01EB001XB61 | U1 NH3 VAP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | - | DCDAS | LCP | - | - | -
=C10QCG01EB001XB62 | U1 NH3 VAP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | - | DCDAS | LCP | - | - | -
=C10QCG01EB001XB69 | U1 NH3 VAP TRIP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | - | DCDAS | LCP | - | - | -
=C10QCG01EB001XQ23 | U1 NH3 VAP HEAT CTRL SP | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | - | DCDAS | LCP | - | - | -
=C10QCM01BP004XG01 | U1 NH3 VAP PSV VENT PSH | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCM01BP005XG01 | U1 NH3 ACC PSV VENT PS H | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C10XLA01QM063XB62 | U1 NH3 ACC SPY XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10XLA01QM063XG01 | U1 NH3 ACC SPY XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM063XG02 | U1 NH3 ACC SPY XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM063XG33 | U1 NH3 ACC SPY XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C10XLA01QM063XG34 | U1 NH3 ACC SPY XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C10XLA01QM064XB62 | U1 NH3 VAP SPY XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10XLA01QM064XG01 | U1 NH3 VAP SPY XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM064XG02 | U1 NH3 VAP SPY XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM064XG33 | U1 NH3 VAP SPY XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C10XLA01QM064XG34 | U1 NH3 VAP SPY XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6003 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C10QCM01BL001XG01 | U1 NH3 DIL TK LIS H | D-DI | 24VDC | S | - | 3500 | - | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10QCM01BL001XG03 | U1 NH3 DIL TK LIS HH | D-DI | 24VDC | S | 4000 | - | - | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10QCM01BL001XG52 | U1 NH3 DIL TK LIS L | D-DI | 24VDC | S | - | - | 2400 | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10QCM01BL001XG54 | U1 NH3 DIL TK LIS LL | D-DI | 24VDC | S | - | - | - | 600 | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10QCM01BL001XH11 | U1 NH3 DIL TK LIS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01BL001XH13 | U1 NH3 DIL TK LIS HH LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01BL001XH62 | U1 NH3 DIL TK LIS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01BL001XH64 | U1 NH3 DIL TK LIS LL LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01BL301XQ01 | U1 NH3 DIL TK LIT | D-AI | 4-20mA | S | - | - | - | 600 | mm | NO | YES | - | - | - | 0 | 4328 | mmH2O | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C10QCM01BP301XQ01 | U1 WASTE NH3 WTR PP INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C10QCM01BQ301XQ01 | U1 NH3 DIL TK AIT (PH) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 14 | pH | 0 | 14 | pH | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | PH Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C10QCM01GP001XB01 | U1 WASTE NH3 WTR PP ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | MCC | DCDAS | - | - | -
=C10QCM01GP001XB20 | U1 WASTE NH3 WTR PP LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | LCP | DCDAS | - | - | -
=C10QCM01GP001XB41 | U1 WASTE NH3 WTR PP LOC START CMD | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | LCP | DCDAS | - | - | -
=C10QCM01GP001XB42 | U1 WASTE NH3 WTR PP LOC STOP CMD | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | LCP | DCDAS | - | - | -
=C10QCM01GP001XB49 | U1 WASTE NH3 WTR PP ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | MCC | DCDAS | - | - | -
=C10QCM01GP001XB50 | U1 WASTE NH3 WTR PP PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | MCC | DCDAS | - | - | -
=C10QCM01GP001XB55 | U1 WASTE NH3 WTR PP FAULT LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01GP001XB61 | U1 WASTE NH3 WTR PP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | DCDAS | MCC | - | - | -
=C10QCM01GP001XB62 | U1 WASTE NH3 WTR PP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | DCDAS | MCC | - | - | -
=C10QCM01GP001XB63 | U1 WASTE NH3 WTR PP START LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01GP001XB64 | U1 WASTE NH3 WTR PP STOP LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01GP001XB69 | U1 WASTE NH3 WTR PP STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | DCDAS | MCC | - | - | -
=C10QCM01GP001XB78 | U1 WASTE NH3 WTR PP REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | MCC | DCDAS | - | - | -
=C10QCM01QM032XB75 | TO TK TRUCK HV VLV LCP OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01QM032XB76 | TO TK TRUCK HV VLV LCP CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01QM032XG01 | TO TK TRUCK HV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Hand Valve | FIELD | DCDAS | - | - | -
=C10QCM01QM032XG02 | TO TK TRUCK HV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Hand Valve | FIELD | DCDAS | - | - | -
=C10QCM01QM034XB75 | U1 NH3 DIL TANK TO L-P SUMP HV LCP OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01QM034XB76 | U1 NH3 DIL TANK TO L-P SUMP HV LCP CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01QM034XG01 | U1 NH3 DIL TANK TO L-P SUMP HV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Hand Valve | FIELD | DCDAS | - | - | -
=C10QCM01QM034XG02 | U1 NH3 DIL TANK TO L-P SUMP HV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Hand Valve | FIELD | DCDAS | - | - | -
=C10QCM01QM081XB01 | U1 NH3 DIL TK OUTL MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCM01QM081XB02 | U1 NH3 DIL TK OUTL MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCM01QM081XB20 | U1 NH3 DIL TK OUTL MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCM01QM081XB49 | U1 NH3 DIL TK OUTL MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | MCC | DCDAS | - | - | -
=C10QCM01QM081XB50 | U1 NH3 DIL TK OUTL MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | MCC | DCDAS | - | - | -
=C10QCM01QM081XB61 | U1 NH3 DIL TK OUTL MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | MCC | - | - | -
=C10QCM01QM081XB62 | U1 NH3 DIL TK OUTL MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | MCC | - | - | -
=C10QCM01QM081XB63 | U1 NH3 DIL TK OUTL MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C10QCM01QM081XB64 | U1 NH3 DIL TK OUTL MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C10QCM01QM081XB75 | U1 NH3 DIL TK OUTL MOV-LCP OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01QM081XB76 | U1 NH3 DIL TK OUTL MOV-LCP CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C10QCM01QM081XB78 | U1 NH3 DIL TK OUTL MOV-LCP LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C10QCM01QM081XB87 | U1 NH3 DIL TK OUTL MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCM01QM081XB88 | U1 NH3 DIL TK OUTL MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCM01QM081XG33 | U1 NH3 DIL TK OUTL MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCM01QM081XG34 | U1 NH3 DIL TK OUTL MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C10QCM01QM081XG35 | U1 NH3 DIL TK OUTL MOV-LCP OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C10QCM01QM081XG36 | U1 NH3 DIL TK OUTL MOV-LCP CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C10QCM01XD301XB95 | U1 NH3 DIL TK & WW PP LCP LAMP TEST | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | - | LCP | DCDAS | - | - | -
=C10XLA01QM081XB01 | FR PW TO U1 NH3 DIL TK MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM081XB02 | FR PW TO U1 NH3 DIL TK MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM081XB20 | FR PW TO U1 NH3 DIL TK MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM081XB49 | FR PW TO U1 NH3 DIL TK MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C10XLA01QM081XB50 | FR PW TO U1 NH3 DIL TK MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C10XLA01QM081XB61 | FR PW TO U1 NH3 DIL TK MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C10XLA01QM081XB62 | FR PW TO U1 NH3 DIL TK MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C10XLA01QM081XB63 | FR PW TO U1 NH3 DIL TK MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10XLA01QM081XB64 | FR PW TO U1 NH3 DIL TK MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10XLA01QM081XB87 | FR PW TO U1 NH3 DIL TK MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM081XB88 | FR PW TO U1 NH3 DIL TK MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM081XG33 | FR PW TO U1 NH3 DIL TK MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM081XG34 | FR PW TO U1 NH3 DIL TK MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XLA01QM081XG35 | FR PW TO U1 NH3 DIL TK MOV-LCP OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C10XLA01QM081XG36 | FR PW TO U1 NH3 DIL TK MOV-LCP CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC1-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20QCM01QM081XB78 | U2 NH3 DIL TK OUTL MOV-LCP LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#1) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C20QCG01BQ301XB48 | U2 NH3 UNLOADING COMP AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCG01BQ301XQ01 | U2 NH3 UNLOADING COMP AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCG01BQ302XQ01 | U2 NH3 STG TK AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCG01BQ303XQ01 | U2 NH3 STG TK AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCG01BQ304XQ01 | U2 NH3 ACC AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCG01BQ305XQ01 | U2 NH3 VAP AIT (GD) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCG01XD301XB96 | U2 NH3 LOC ALM CMN EMRG | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | LCP | DCDAS | - | - | -
=C20QCG11BL001XG01 | U2 NH3 UNLOAD COMP LIQ TRAP LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | Float Level Switch | FIELD | DCDAS | - | - | -
=C20QCG11BL001XH11 | U2 NH3 UNLOAD COMP LIQ TRAP LSH LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCG11BP002XG01 | U2 NH3 UNLOAD COMP PDS H | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | D/P Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCG11BP002XH11 | U2 NH3 UNLOAD COMP PDS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCG11BP003XG52 | U2 NH3 UNLOAD COMP SUCTION PS L | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCG11BP003XH62 | U2 NH3 UNLOAD COMP SUCTION PS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCG11BP004XG01 | U2 NH3 UNLOAD COMP SUCTION PS H | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCG11BP004XH11 | U2 NH3 UNLOAD COMP SUCTION PS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCG11BT001XG01 | U2 NH3 UNLOAD COMP SUCTION TS H | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | Temperature Switch | FIELD | DCDAS | - | - | -
=C20QCG11BT001XH11 | U2 NH3 UNLOAD COMP SUCTION TS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCG11GQ001XB01 | U2 NH3 UNLOAD COMP ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | MCC | DCDAS | - | - | -
=C20QCG11GQ001XB20 | U2 NH3 UNLOAD COMP LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | LCP | DCDAS | - | - | -
=C20QCG11GQ001XB41 | U2 NH3 UNLOAD COMP LOC START CMD | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | LCP | DCDAS | - | - | -
=C20QCG11GQ001XB42 | U2 NH3 UNLOAD COMP LOC STOP CMD | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | LCP | DCDAS | - | - | -
=C20QCG11GQ001XB49 | U2 NH3 UNLOAD COMP ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | MCC | DCDAS | - | - | -
=C20QCG11GQ001XB50 | U2 NH3 UNLOAD COMP PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | MCC | DCDAS | - | - | -
=C20QCG11GQ001XB55 | U2 NH3 UNLOAD COMP FAULT LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCG11GQ001XB61 | U2 NH3 UNLOAD COMP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | DCDAS | MCC | - | - | -
=C20QCG11GQ001XB62 | U2 NH3 UNLOAD COMP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | DCDAS | MCC | - | - | -
=C20QCG11GQ001XB63 | U2 NH3 UNLOAD COMP START LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCG11GQ001XB64 | U2 NH3 UNLOAD COMP STOP LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCG11GQ001XB69 | U2 NH3 UNLOAD COMP STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | DCDAS | MCC | - | - | -
=C20QCG11GQ001XB78 | U2 NH3 UNLOAD COMP REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | - | MCC | DCDAS | - | - | -
=C20QCM01BP001XG01 | U2 NH3 UNLOAD COMP PSV VENT PS H | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCV11BP001XG52 | U2 NH3 UNLOAD COMP OIL PS L | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCV11BP001XH62 | U2 NH3 UNLOAD COMP OIL PS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | LCP LAMP | DCDAS | LCP | - | - | -
=C20XLA01QM062XB62 | U2 NH3 UNLOAD COMPR SPY XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20XLA01QM062XG01 | U2 NH3 UNLOAD COMP SPY XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM062XG02 | U2 NH3 UNLOAD COMP SPY XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM062XG33 | U2 NH3 UNLOAD COMP SPY XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20XLA01QM062XG34 | U2 NH3 UNLOAD COMP SPY XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6001 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20QCG01BP302XQ01 | FR U2 NH3 STG TK TO U2 NH3 ACC PIT | D-AI | 4-20mA | S | - | 0.6 | 0.38 | - | MPaG | NO | YES | - | - | - | 0 | 1.112 | MPaG | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCG01BQ302XB48 | U2 NH3 STG TK AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCG01BQ303XB48 | U2 NH3 STG TK AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCL01BF301XB27 | TO U2 NH3 STG TK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 30 | m3/hr | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C20QCL01BF301XQ01 | TO U2 NH3 STG TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 30 | m3/hr | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C20QCL01BF301XQ23 | TO U2 NH3 STG TK LOC IND | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 30 | m3/hr | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Local Indicator | DCDAS | LCP | - | - | -
=C20QCL01BL001XG01 | U2 NH3 STG TK LIS H | D-DI | 24VDC | S | - | 2650 | - | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20QCL01BL001XG52 | U2 NH3 STG TK LIS L | D-DI | 24VDC | S | - | - | 320 | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20QCL01BL001XH11 | U2 NH3 STG TK LIS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCL01BL001XH62 | U2 NH3 STG TK LIS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCL01BL301XQ01 | U2 NH3 STG TK LIT | D-AI | 4-20mA | S | - | 2650 | 320 | - | mm | NO | YES | - | - | - | 200 | 3200 | mm | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Radar Level Transmitter | FIELD | DCDAS | - | - | -
=C20QCL01BL301XQ23 | U2 NH3 STG TK LIT LOC IND | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 200 | 3200 | mm | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Local Indicator | DCDAS | FIELD | - | - | -
=C20QCL01BP001XG01 | U2 NH3 STG TK PS H | D-DI | 24VDC | S | - | 1.28 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCL01BP001XG52 | U2 NH3 STG TK PS L | D-DI | 24VDC | S | - | - | 0.82 | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCL01BP001XH11 | U2 NH3 STG TK PS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCL01BP001XH62 | U2 NH3 STG TK PS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCL01BP301XQ01 | FR U2 NH3 STG TK TO U2 NH3 VAP PIT | D-AI | 4-20mA | S | 1.64 | 1.28 | 0.82 | 0.55 | MPaG | NO | YES | - | - | - | 0 | 2.284 | MPaG | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCL01BT301XH11 | U2 NH3 STG TK TS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCL01BT301XH62 | U2 NH3 STG TK TS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCL01BT301XQ01 | U2 NH3 STG TK TIT | D-AI | 4-20mA | S | - | 42 | 22 | - | ℃ | NO | YES | - | - | - | -50 | 100 | ℃ | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C20QCL01QM061XB61 | FR U2 NH3 LORRY TO U2 NH3 STG TK XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C20QCL01QM061XG01 | FR U2 NH3 LORRY TO U2 NH3 STG TK XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCL01QM061XG02 | FR U2 NH3 LORRY TO U2 NH3 STG TK XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCL01QM061XG33 | FR U2 NH3 LORRY TO U2 NH3 STG TK XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C20QCL01QM061XG34 | FR U2 NH3 LORRY TO U2 NH3 STG TK XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C20QCL01QM081XB01 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCL01QM081XB02 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCL01QM081XB20 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCL01QM081XB49 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | MCC | DCDAS | - | - | -
=C20QCL01QM081XB50 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | MCC | DCDAS | - | - | -
=C20QCL01QM081XB61 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | MCC | - | - | -
=C20QCL01QM081XB62 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | MCC | - | - | -
=C20QCL01QM081XB63 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C20QCL01QM081XB64 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C20QCL01QM081XB87 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCL01QM081XB88 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCL01QM081XG33 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCL01QM081XG34 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCL01QM081XG35 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C20QCL01QM081XG36 | FR U2 NH3 STG TK TO U2 NH3 VAP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C20QCL01XD301XB95 | U2 NH3 STG TK LCP LAMP TEST | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | - | LCP | DCDAS | - | - | -
=C20QCM01BP002XG01 | U2 NH3 LORRY PSV VENT PS H | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCM01BP003XG01 | U2 NH3 UNLOAD STG TK PSV VENT PS H | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20XLA01QM061XB62 | U2 NH3 STG TK SPY XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20XLA01QM061XG01 | U2 NH3 STG TK SPY XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM061XG02 | U2 NH3 STG TK SPY XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM061XG33 | U2 NH3 STG TK SPY XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20XLA01QM061XG34 | U2 NH3 STG TK SPY XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6002 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20QCG01BP001XG01 | U2 NH3 ACC PS H | D-DI | 24VDC | S | - | 0.6 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCG01BP301XQ01 | FR U2 NH3 VAP TO U2 NH3 STG TK PIT | D-AI | 4-20mA | S | - | 1.28 | 0.82 | - | MPaG | NO | YES | - | - | - | 0 | 2.284 | MPaG | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCG01BP303XQ01 | FR NH3 ACC TO U2 HRSG NH3 MIXER PIT | D-AI | 4-20mA | S | - | 0.6 | 0.38 | - | MPaG | NO | YES | - | - | - | 0 | 1.112 | MPaG | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCG01BQ304XB48 | U2 NH3 ACC AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCG01BQ305XB48 | U2 NH3 VAP AIT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | NH3 Gas detector (Transmitter) | LCP | DCDAS | - | - | -
=C20QCG01BT301XQ01 | FR U2 NH3 VAP TO U2 NH3 STG TK TIT | D-AI | 4-20mA | S | - | 42 | 22 | - | ℃ | NO | YES | - | - | - | -50 | 100 | ℃ | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C20QCG01BT302XQ01 | U2 NH3 VAP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | Temperature Transmitter | LCP | DCDAS | - | - | -
=C20QCG01EB001XB01 | U2 NH3 VAP ON RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | - | LCP | DCDAS | - | - | -
=C20QCG01EB001XB20 | U2 NH3 VAP LOC STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | - | LCP | DCDAS | - | - | -
=C20QCG01EB001XB40 | U2 NH3 VAP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | - | LCP | DCDAS | - | - | -
=C20QCG01EB001XB61 | U2 NH3 VAP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | - | DCDAS | LCP | - | - | -
=C20QCG01EB001XB62 | U2 NH3 VAP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | - | DCDAS | LCP | - | - | -
=C20QCG01EB001XB69 | U2 NH3 VAP TRIP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | - | DCDAS | LCP | - | - | -
=C20QCG01EB001XQ23 | U2 NH3 VAP HEAT CTRL SP | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | - | DCDAS | LCP | - | - | -
=C20QCM01BP004XG01 | U2 NH3 VAP PSV VENT PS H | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCM01BP005XG01 | U2 NH3 ACC PSV VENT PS H | D-DI | 24VDC | S | - | 0.06 | - | - | MPaG | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C20XLA01QM063XB62 | U2 NH3 ACC SPY XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20XLA01QM063XG01 | U2 NH3 ACC SPY XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM063XG02 | U2 NH3 ACC SPY XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM063XG33 | U2 NH3 ACC SPY XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20XLA01QM063XG34 | U2 NH3 ACC SPY XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20XLA01QM064XB62 | U2 NH3 VAP SPY XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20XLA01QM064XG01 | U2 NH3 VAP SPY XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM064XG02 | U2 NH3 VAP SPY XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM064XG33 | U2 NH3 VAP SPY XV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20XLA01QM064XG34 | U2 NH3 VAP SPY XV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6003 | On off Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20QCM01BL001XG01 | U2 NH3 DIL TK LIS H | D-DI | 24VDC | S | - | 3500 | - | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20QCM01BL001XG03 | U2 NH3 DIL TK LIS HH | D-DI | 24VDC | S | 4000 | - | - | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20QCM01BL001XG52 | U2 NH3 DIL TK LIS L | D-DI | 24VDC | S | - | - | 2400 | - | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20QCM01BL001XG54 | U2 NH3 DIL TK LIS LL | D-DI | 24VDC | S | - | - | - | 600 | mm | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20QCM01BL001XH11 | U2 NH3 DIL TK LIS H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCM01BL001XH13 | U2 NH3 DIL TK LIS HH LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCM01BL001XH62 | U2 NH3 DIL TK LIS L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCM01BL001XH64 | U2 NH3 DIL TK LIS LL LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | LCP LAMP | DCDAS | LCP | - | - | -
=C20QCM01BL301XQ01 | U2 NH3 DIL TK LIT | D-AI | 4-20mA | S | - | - | - | 600 | mm | NO | YES | - | - | - | 0 | 4328 | mmH2O | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C20QCM01BP301XQ01 | U2 WASTE NH3 WTR PP INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C20QCM01BQ301XQ01 | U2 NH3 DIL TK AIT (PH) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 14 | pH | 0 | 14 | pH | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | PH Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C20QCM01GP001XB01 | U2 WASTE NH3 WTR PP ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | MCC | DCDAS | - | - | -
=C20QCM01GP001XB20 | U2 WASTE NH3 WTR PP LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | LCP | DCDAS | - | - | -
=C20QCM01GP001XB41 | U2 WASTE NH3 WTR PP LOC START CMD | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | LCP | DCDAS | - | - | -
=C20QCM01GP001XB42 | U2 WASTE NH3 WTR PP LOC STOP CMD | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | LCP | DCDAS | - | - | -
=C20QCM01GP001XB49 | U2 WASTE NH3 WTR PP ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | MCC | DCDAS | - | - | -
=C20QCM01GP001XB50 | U2 WASTE NH3 WTR PP PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | MCC | DCDAS | - | - | -
=C20QCM01GP001XB55 | U2 WASTE NH3 WTR PP FAULT LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | DCDAS | LCP | - | - | -
=C20QCM01GP001XB61 | U2 WASTE NH3 WTR PP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | DCDAS | MCC | - | - | -
=C20QCM01GP001XB62 | U2 WASTE NH3 WTR PP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | DCDAS | MCC | - | - | -
=C20QCM01GP001XB63 | U2 WASTE NH3 WTR PP START LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | DCDAS | LCP | - | - | -
=C20QCM01GP001XB64 | U2 WASTE NH3 WTR PP STOP LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | DCDAS | LCP | - | - | -
=C20QCM01GP001XB69 | U2 WASTE NH3 WTR PP STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | DCDAS | MCC | - | - | -
=C20QCM01GP001XB78 | U2 WASTE NH3 WTR PP REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | MCC | DCDAS | - | - | -
=C20QCM01QM032XB75 | OUT OF U2 NH3 DIL TK HV VLV LCP OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Hand Valve | DCDAS | LCP | - | - | -
=C20QCM01QM032XB76 | OUT OF U2 NH3 DIL TK HV VLV LCP CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Hand Valve | DCDAS | LCP | - | - | -
=C20QCM01QM032XG01 | OUT OF U2 NH3 DIL TK HV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Hand Valve | FIELD | DCDAS | - | - | -
=C20QCM01QM032XG02 | OUT OF U2 NH3 DIL TK HV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Hand Valve | FIELD | DCDAS | - | - | -
=C20QCM01QM034XB75 | OUT OF U2 NH3 DIL TK HV LCP OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Hand Valve | DCDAS | LCP | - | - | -
=C20QCM01QM034XB76 | OUT OF U2 NH3 DIL TK HV LCP CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Hand Valve | DCDAS | LCP | - | - | -
=C20QCM01QM034XG01 | OUT OF U2 NH3 DIL TK HV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Hand Valve | FIELD | DCDAS | - | - | -
=C20QCM01QM034XG02 | OUT OF U2 NH3 DIL TK HV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Hand Valve | FIELD | DCDAS | - | - | -
=C20QCM01QM081XB01 | U2 NH3 DIL TK OUTL MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCM01QM081XB02 | U2 NH3 DIL TK OUTL MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCM01QM081XB20 | U2 NH3 DIL TK OUTL MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCM01QM081XB49 | U2 NH3 DIL TK OUTL MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | MCC | DCDAS | - | - | -
=C20QCM01QM081XB50 | U2 NH3 DIL TK OUTL MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | MCC | DCDAS | - | - | -
=C20QCM01QM081XB61 | U2 NH3 DIL TK OUTL MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | MCC | - | - | -
=C20QCM01QM081XB62 | U2 NH3 DIL TK OUTL MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | MCC | - | - | -
=C20QCM01QM081XB63 | U2 NH3 DIL TK OUTL MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C20QCM01QM081XB64 | U2 NH3 DIL TK OUTL MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | FIELD | - | - | -
=C20QCM01QM081XB75 | U2 NH3 DIL TK OUTL MOV-LCP OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | LCP | - | - | -
=C20QCM01QM081XB76 | U2 NH3 DIL TK OUTL MOV-LCP CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | DCDAS | LCP | - | - | -
=C20QCM01QM081XB87 | U2 NH3 DIL TK OUTL MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCM01QM081XB88 | U2 NH3 DIL TK OUTL MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCM01QM081XG33 | U2 NH3 DIL TK OUTL MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCM01QM081XG34 | U2 NH3 DIL TK OUTL MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | FIELD | DCDAS | - | - | -
=C20QCM01QM081XG35 | U2 NH3 DIL TK OUTL MOV-LCP OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C20QCM01QM081XG36 | U2 NH3 DIL TK OUTL MOV-LCP CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve with Bellow Seal) | LCP | DCDAS | - | - | -
=C20QCM01XD301XB95 | U2 NH3 DIL TK & WW PP LCP LAMP TEST | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | - | LCP | DCDAS | - | - | -
=C20XLA01QM081XB01 | FR PW TO U2 NH3 DIL TK MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM081XB02 | FR PW TO U2 NH3 DIL TK MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM081XB20 | FR PW TO U2 NH3 DIL TK MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM081XB49 | FR PW TO U2 NH3 DIL TK MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C20XLA01QM081XB50 | FR PW TO U2 NH3 DIL TK MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C20XLA01QM081XB61 | FR PW TO U2 NH3 DIL TK MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C20XLA01QM081XB62 | FR PW TO U2 NH3 DIL TK MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C20XLA01QM081XB63 | FR PW TO U2 NH3 DIL TK MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20XLA01QM081XB64 | FR PW TO U2 NH3 DIL TK MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20XLA01QM081XB87 | FR PW TO U2 NH3 DIL TK MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM081XB88 | FR PW TO U2 NH3 DIL TK MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM081XG33 | FR PW TO U2 NH3 DIL TK MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM081XG34 | FR PW TO U2 NH3 DIL TK MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20XLA01QM081XG35 | FR PW TO U2 NH3 DIL TK MOV-LCP OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C20XLA01QM081XG36 | FR PW TO U2 NH3 DIL TK MOV-LCP CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AMMONIA STORAGE AND SUPPLY SYSTEM (CC#2) | WWT | TC2-1-KNM02-D6004 | Moter Operated Control Valve (Gate Valve) | LCP | DCDAS | - | - | -
=C00LBG01BF301XQ01 | TPC STM LINE FR EX STM OF U9 & U10 FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 4700 | m3/hr | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Vortex Flow Totalizer | FIELD | DCDAS | - | - | -
=C00LBG01BP301XQ01 | TPC STM LINE FR EX STM OF U9 & U10 PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 7.56 | MPaG | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00LBG01BT301XQ01 | TPC STM LINE FR EX STM OF U9 & U10 TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 600 | ℃ | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00LBG01QM081XB01 | TPC STM LINE FR EX STM OF U9 & U10 MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LBG01QM081XB02 | TPC STM LINE FR EX STM OF U9 & U10 MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LBG01QM081XB20 | TPC STM LINE FR EX STM OF U9 & U10 MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LBG01QM081XB49 | TPC STM LINE FR EX STM OF U9 & U10 MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00LBG01QM081XB50 | TPC STM LINE FR EX STM OF U9 & U10 MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00LBG01QM081XB61 | TPC STM LINE FR EX STM OF U9 & U10 MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00LBG01QM081XB62 | TPC STM LINE FR EX STM OF U9 & U10 MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00LBG01QM081XB63 | TPC STM LINE FR EX STM OF U9 & U10 MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00LBG01QM081XB64 | TPC STM LINE FR EX STM OF U9 & U10 MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00LBG01QM081XB87 | TPC STM LINE FR EX STM OF U9 & U10 MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LBG01QM081XB88 | TPC STM LINE FR EX STM OF U9 & U10 MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LBG01QM081XG33 | TPC STM LINE FR EX STM OF U9 & U10 MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LBG01QM081XG34 | TPC STM LINE FR EX STM OF U9 & U10 MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6001 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LAH01QM061XB62 | TO CNDS HDR XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00LAH01QM061XG01 | TO CNDS HDR XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LAH01QM061XG02 | TO CNDS HDR XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LAH01QM062XB62 | TO CNDS COLL XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00LAH01QM062XG01 | TO CNDS COLL XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LAH01QM062XG02 | TO CNDS COLL XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00LBG01BF302XQ01 | FR STM HEADER FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 620 | m3/hr | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6002 | Vortex Flow Totalizer | FIELD | DCDAS | - | - | -
=C00LBG01BP302XQ01 | FR STM HEADER PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 8.12 | MPaG | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6002 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00LBG01BT302XQ01 | FR STM HEADER TIT | D-AI | 4-20mA | S | - | - | 218 | - | ℃ | NO | YES | - | - | - | 0 | 700 | ℃ | AUXILIARY STEAM SYSTEM (COMMON) | MCB | TC0-1-TSM02-D6002 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00LBG01QN002XG01 | AWWTS START-UP SILENCER INL CV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00LBG01QN002XG02 | AWWTS START-UP SILENCER INL CV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00LBG01QN002XQ01 | AWWTS START-UP SILENCER INL CV-ZT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00LBG01QN002XQ23 | AWWTS START-UP SILENCER INL CV-PY | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | AUXILIARY STEAM SYSTEM (COMMON) | WWT | TC0-1-TSM02-D6002 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C00GMZ01XD801AXB41 | WW SUMP FOR CABLE TUNL #1 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD801AXJ51 | WW SUMP FOR CABLE TUNL #1 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD801BXB41 | WW SUMP FOR CABLE TUNL #1 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD801BXJ51 | WW SUMP FOR CABLE TUNL #1 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD801XB40 | WW SUMP FOR CABLE TUNL #1 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD801XG01 | WW SUMP FOR CABLE TUNL #1 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD801XG03 | WW SUMP FOR CABLE TUNL #1 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD801XG52 | WW SUMP FOR CABLE TUNL #1 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD801XG54 | WW SUMP FOR CABLE TUNL #1 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD802AXB41 | WW SUMP FOR CABLE TUNL #2 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD802AXJ51 | WW SUMP FOR CABLE TUNL #2 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD802BXB41 | WW SUMP FOR CABLE TUNL #2 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD802BXJ51 | WW SUMP FOR CABLE TUNL #2 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD802XB40 | WW SUMP FOR CABLE TUNL #2 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD802XG01 | WW SUMP FOR CABLE TUNL #2 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD802XG03 | WW SUMP FOR CABLE TUNL #2 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD802XG52 | WW SUMP FOR CABLE TUNL #2 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD802XG54 | WW SUMP FOR CABLE TUNL #2 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD803AXB41 | WW SUMP FOR CABLE TUNL #3 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD803AXJ51 | WW SUMP FOR CABLE TUNL #3 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD803BXB41 | WW SUMP FOR CABLE TUNL #3 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD803BXJ51 | WW SUMP FOR CABLE TUNL #3 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD803XB40 | WW SUMP FOR CABLE TUNL #3 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD803XG01 | WW SUMP FOR CABLE TUNL #3 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD803XG03 | WW SUMP FOR CABLE TUNL #3 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD803XG52 | WW SUMP FOR CABLE TUNL #3 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD803XG54 | WW SUMP FOR CABLE TUNL #3 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD804AXB41 | WW SUMP FOR CABLE TUNL #4 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD804AXJ51 | WW SUMP FOR CABLE TUNL #4 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD804BXB41 | WW SUMP FOR CABLE TUNL #4 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD804BXJ51 | WW SUMP FOR CABLE TUNL #4 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD804XB40 | WW SUMP FOR CABLE TUNL #4 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD804XG01 | WW SUMP FOR CABLE TUNL #4 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD804XG03 | WW SUMP FOR CABLE TUNL #4 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD804XG52 | WW SUMP FOR CABLE TUNL #4 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD804XG54 | WW SUMP FOR CABLE TUNL #4 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD805AXB41 | WW SUMP FOR CABLE TUNL #5 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD805AXJ51 | WW SUMP FOR CABLE TUNL #5 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD805BXB41 | WW SUMP FOR CABLE TUNL #5 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD805BXJ51 | WW SUMP FOR CABLE TUNL #5 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD805XB40 | WW SUMP FOR CABLE TUNL #5 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD805XG01 | WW SUMP FOR CABLE TUNL #5 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD805XG03 | WW SUMP FOR CABLE TUNL #5 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD805XG52 | WW SUMP FOR CABLE TUNL #5 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD805XG54 | WW SUMP FOR CABLE TUNL #5 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD806AXB41 | WW SUMP FOR CABLE TUNL #6 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD806AXJ51 | WW SUMP FOR CABLE TUNL #6 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD806BXB41 | WW SUMP FOR CABLE TUNL #6 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD806BXJ51 | WW SUMP FOR CABLE TUNL #6 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD806XB40 | WW SUMP FOR CABLE TUNL #6 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD806XG01 | WW SUMP FOR CABLE TUNL #6 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD806XG03 | WW SUMP FOR CABLE TUNL #6 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD806XG52 | WW SUMP FOR CABLE TUNL #6 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD806XG54 | WW SUMP FOR CABLE TUNL #6 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD807AXB41 | WW SUMP FOR CABLE TUNL #7 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD807AXJ51 | WW SUMP FOR CABLE TUNL #7 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD807BXB41 | WW SUMP FOR CABLE TUNL #7 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD807BXJ51 | WW SUMP FOR CABLE TUNL #7 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD807XB40 | WW SUMP FOR CABLE TUNL #7 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD807XG01 | WW SUMP FOR CABLE TUNL #7 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD807XG03 | WW SUMP FOR CABLE TUNL #7 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD807XG52 | WW SUMP FOR CABLE TUNL #7 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD807XG54 | WW SUMP FOR CABLE TUNL #7 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD808AXB41 | WW SUMP FOR CABLE TUNL #8 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD808AXJ51 | WW SUMP FOR CABLE TUNL #8 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD808BXB41 | WW SUMP FOR CABLE TUNL #8 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD808BXJ51 | WW SUMP FOR CABLE TUNL #8 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD808XB40 | WW SUMP FOR CABLE TUNL #8 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD808XG01 | WW SUMP FOR CABLE TUNL #8 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD808XG03 | WW SUMP FOR CABLE TUNL #8 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD808XG52 | WW SUMP FOR CABLE TUNL #8 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD808XG54 | WW SUMP FOR CABLE TUNL #8 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6303 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD809AXB41 | WW SUMP FOR CABLE TUNL #9 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD809AXJ51 | WW SUMP FOR CABLE TUNL #9 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD809BXB41 | WW SUMP FOR CABLE TUNL #9 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD809BXJ51 | WW SUMP FOR CABLE TUNL #9 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD809XB40 | WW SUMP FOR CABLE TUNL #9 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD809XG01 | WW SUMP FOR CABLE TUNL #9 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD809XG03 | WW SUMP FOR CABLE TUNL #9 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD809XG52 | WW SUMP FOR CABLE TUNL #9 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD809XG54 | WW SUMP FOR CABLE TUNL #9 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD810AXB41 | WW SUMP FOR CABLE TUNL #10 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD810AXJ51 | WW SUMP FOR CABLE TUNL #10 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD810BXB41 | WW SUMP FOR CABLE TUNL #10 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD810BXJ51 | WW SUMP FOR CABLE TUNL #10 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD810XB40 | WW SUMP FOR CABLE TUNL #10 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD810XG01 | WW SUMP FOR CABLE TUNL #10 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD810XG03 | WW SUMP FOR CABLE TUNL #10 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD810XG52 | WW SUMP FOR CABLE TUNL #10 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD810XG54 | WW SUMP FOR CABLE TUNL #10 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD811AXB41 | WW SUMP FOR CABLE TUNL #11 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD811AXJ51 | WW SUMP FOR CABLE TUNL #11 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD811BXB41 | WW SUMP FOR CABLE TUNL #11 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD811BXJ51 | WW SUMP FOR CABLE TUNL #11 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD811XB40 | WW SUMP FOR CABLE TUNL #11 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD811XG01 | WW SUMP FOR CABLE TUNL #11 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD811XG03 | WW SUMP FOR CABLE TUNL #11 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD811XG52 | WW SUMP FOR CABLE TUNL #11 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD811XG54 | WW SUMP FOR CABLE TUNL #11 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD812AXB41 | WW SUMP FOR CABLE TUNL #12 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD812AXJ51 | WW SUMP FOR CABLE TUNL #12 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD812BXB41 | WW SUMP FOR CABLE TUNL #12 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD812BXJ51 | WW SUMP FOR CABLE TUNL #12 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD812XB40 | WW SUMP FOR CABLE TUNL #12 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD812XG01 | WW SUMP FOR CABLE TUNL #12 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD812XG03 | WW SUMP FOR CABLE TUNL #12 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD812XG52 | WW SUMP FOR CABLE TUNL #12 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD812XG54 | WW SUMP FOR CABLE TUNL #12 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6304 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD813AXB41 | WW SUMP FOR CABLE TUNL #13 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD813AXJ51 | WW SUMP FOR CABLE TUNL #13 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD813BXB41 | WW SUMP FOR CABLE TUNL #13 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD813BXJ51 | WW SUMP FOR CABLE TUNL #13 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD813XB40 | WW SUMP FOR CABLE TUNL #13 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD813XG01 | WW SUMP FOR CABLE TUNL #13 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD813XG03 | WW SUMP FOR CABLE TUNL #13 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD813XG52 | WW SUMP FOR CABLE TUNL #13 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD813XG54 | WW SUMP FOR CABLE TUNL #13 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD814AXB41 | WW SUMP FOR CABLE TUNL #14 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD814AXJ51 | WW SUMP FOR CABLE TUNL #14 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD814BXB41 | WW SUMP FOR CABLE TUNL #14 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD814BXJ51 | WW SUMP FOR CABLE TUNL #14 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD814XB40 | WW SUMP FOR CABLE TUNL #14 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD814XG01 | WW SUMP FOR CABLE TUNL #14 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD814XG03 | WW SUMP FOR CABLE TUNL #14 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD814XG52 | WW SUMP FOR CABLE TUNL #14 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD814XG54 | WW SUMP FOR CABLE TUNL #14 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD815AXB41 | WW SUMP FOR CABLE TUNL #15 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD815AXJ51 | WW SUMP FOR CABLE TUNL #15 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD815BXB41 | WW SUMP FOR CABLE TUNL #15 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD815BXJ51 | WW SUMP FOR CABLE TUNL #15 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD815XB40 | WW SUMP FOR CABLE TUNL #15 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD815XG01 | WW SUMP FOR CABLE TUNL #15 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD815XG03 | WW SUMP FOR CABLE TUNL #15 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD815XG52 | WW SUMP FOR CABLE TUNL #15 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD815XG54 | WW SUMP FOR CABLE TUNL #15 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD816AXB41 | WW SUMP FOR CABLE TUNL #16 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD816AXJ51 | WW SUMP FOR CABLE TUNL #16 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD816BXB41 | WW SUMP FOR CABLE TUNL #16 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD816BXJ51 | WW SUMP FOR CABLE TUNL #16 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD816XB40 | WW SUMP FOR CABLE TUNL #16 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD816XG01 | WW SUMP FOR CABLE TUNL #16 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD816XG03 | WW SUMP FOR CABLE TUNL #16 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD816XG52 | WW SUMP FOR CABLE TUNL #16 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C00GMZ01XD816XG54 | WW SUMP FOR CABLE TUNL #16 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CABLE TUNNEL DRAINAGE COLLECTION SYSTEM (COMMON) | TUNL1 | TC0-1-UWM02-D6305 | - | LCP | DCDAS | - | - | -
=C10PAB01BT305XQ01 | U1 CWMS TIT (AVG OF =C10PAB01BT301/302/303/304) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 100 | ℃ | CIRCULATING WATER MONITORING SYSTEM | ST1 | ITB part 8 sec11 | - | CWMS PLC | DCDAS | - | - | -
=C10PAC01FF301XQ01 | U1 CWMS WTR FLOW | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CIRCULATING WATER MONITORING SYSTEM | ST1 | ITB part 8 sec11 | - | CWMS PLC | DCDAS | - | - | -
=C20PAB01BT305XQ01 | U2 CWMS TIT (AVG OF =C20PAB01BT301/302/303/304) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 100 | ℃ | CIRCULATING WATER MONITORING SYSTEM | ST2 | ITB part 8 sec11 | - | CWMS PLC | DCDAS | - | - | -
=C20PAC01FF301XQ01 | U2 CWMS WTR FLOW | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CIRCULATING WATER MONITORING SYSTEM | ST2 | ITB part 8 sec11 | - | CWMS PLC | DCDAS | - | - | -
C1-M-CW-CWP-001-XB75 | U1 CIRC WTR PP A RUN STATUS TO PLC | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CIRCULATING WATER SYSTEM (CC#1) | ST1 | TC1-1-UCM02-D6001 | - | DCDAS | CWMS PLC | - | - | -
C1-M-CW-CWP-002-XB75 | U1 CIRC WTR PP B RUN STATUS TO PLC | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CIRCULATING WATER SYSTEM (CC#1) | ST1 | TC1-1-UCM02-D6001 | - | DCDAS | CWMS PLC | - | - | -
C1-M-CW-CWP-003-XB75 | U1 CIRC WTR PP C RUN STATUS TO PLC | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CIRCULATING WATER SYSTEM (CC#1) | ST1 | TC1-1-UCM02-D6001 | - | DCDAS | CWMS PLC | - | - | -
C2-M-CW-CWP-001-XB75 | U2 CIRC WTR PP A RUN STATUS TO PLC | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CIRCULATING WATER SYSTEM (CC#2) | ST2 | TC2-1-UCM02-D6001 | - | DCDAS | CWMS PLC | - | - | -
C2-M-CW-CWP-002-XB75 | U2 CIRC WTR PP B RUN STATUS TO PLC | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CIRCULATING WATER SYSTEM (CC#2) | ST2 | TC2-1-UCM02-D6001 | - | DCDAS | CWMS PLC | - | - | -
C2-M-CW-CWP-003-XB75 | U2 CIRC WTR PP C RUN STATUS TO PLC | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CIRCULATING WATER SYSTEM (CC#2) | ST2 | TC2-1-UCM02-D6001 | - | DCDAS | CWMS PLC | - | - | -
=C00XMA01GM201XB01 | GT MAINT OVHD CRANE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | EDG | ITB part6 sec17 | - | LCP | DCDAS | - | - | -
=C00XMA01GM201XB49 | GT MAINT OVHD CRANE GLD SYS TRIP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | ST2 | ITB part6 sec17 | - | DCDAS | FIELD | - | - | -
=C00XMV01GM201XB01 | HVY PTS WHSE OVHD CRANE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | EDG | ITB part6 sec17 | - | LCP | DCDAS | - | - | -
=G10XMA01GM201XB01 | U1 GT HALL OVHD CRANE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | GT1 | ITB part6 sec17 | - | LCP | DCDAS | - | - | -
=G10XMA01GM201XB49 | U1 GT HALL OVHD CRANE GLD SYS TRIP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | ST2 | ITB part6 sec17 | - | DCDAS | FIELD | - | - | -
=G10XMA01GM202XB01 | U2 GT HALL OVHD CRANE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | GT2 | ITB part6 sec17 | - | LCP | DCDAS | - | - | -
=G10XMA01GM202XB49 | U2 GT HALL OVHD CRANE GLD SYS TRIP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | GT1 | ITB part6 sec17 | - | DCDAS | FIELD | - | - | -
=S10XMA01GM201XB01 | U1 ST HALL OVHD CRANE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | ST1 | ITB part6 sec17 | - | LCP | DCDAS | - | - | -
=S10XMA01GM202XB01 | U2 ST HALL OVHD CRANE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | ST2 | ITB part6 sec17 | - | LCP | DCDAS | - | - | -
=S10XMA02GM201XB01 | U1 ST HALL SINGLE GIRDER CRANE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | ST1 | ITB part6 sec17 | - | LCP | DCDAS | - | - | -
=S10XMA02GM202XB01 | U2 ST HALL SINGLE GIRDER CRANE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | COMMON | ST2 | ITB part6 sec17 | - | LCP | DCDAS | - | - | -
=C10GHC01QN001XB62 | U1 CNDS STR TK INL CV-REMOTE TRIP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C10GHC01QN001XG01 | U1 CNDS STR TK INL CV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C10GHC01QN001XG02 | U1 CNDS STR TK INL CV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C10GHC01QN001XQ02 | U1 CNDS STR TK INL CV-ZT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C10GHC01QN001XQ23 | U1 CNDS STR TK INL CV-PY | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C10GHF01BF301XB27 | U1 CNDS TRANS PP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 120 | m3/hr | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GHF01BF301XQ01 | U1 CNDS TRANS PP OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 120 | m3/hr | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GHF01BL001XG01 | U1 CNDS STR TK LSH | D-DI | 24VDC | S | - | 13500 | - | - | mm | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C10GHF01BL001XG03 | U1 CNDS STR TK LSHH | D-DI | 24VDC | S | 14250 | - | - | - | mm | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C10GHF01BL001XG52 | U1 CNDS STR TK LSL | D-DI | 24VDC | S | - | - | 1500 | - | mm | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C10GHF01BL001XG54 | U1 CNDS STR TK LSLL | D-DI | 24VDC | S | - | - | - | 750 | mm | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C10GHF01BL301XQ01 | U1 CNDS STR TK LIT | D-AI | 4-20mA | S | 14250 | 13500 | 1500 | 750 | mm | NO | YES | - | - | - | 0 | 14805 | mmH2O | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C10GHF01BP301XQ01 | U1 CNDS TRANS PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C10GHF01BP302XQ01 | U1 CNDS TRANS PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C10GHF01BP303XQ01 | U1 CNDS TRANS PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.708 | 0.671 | MPaG | NO | YES | - | - | - | 0 | 1.49 | MPaG | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C10GHF01BT301XQ01 | U1 CNDS TRANS PP OUTL TIT | D-AI | 4-20mA | S | - | 28 | - | - | ℃ | NO | YES | - | - | - | 0 | 100 | ℃ | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C10GHF01GP501XB01 | U1 CNDS TRANS PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C10GHF01GP501XB49 | U1 CNDS TRANS PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C10GHF01GP501XB50 | U1 CNDS TRANS PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C10GHF01GP501XB61 | U1 CNDS TRANS PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C10GHF01GP501XB62 | U1 CNDS TRANS PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C10GHF01GP501XB69 | U1 CNDS TRANS PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C10GHF01GP501XB78 | U1 CNDS TRANS PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C10GHF01GP501XQ01 | U1 CNDS TRANS PP A AMP | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C10GHF01GP511XB01 | U1 CNDS TRANS PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C10GHF01GP511XB49 | U1 CNDS TRANS PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C10GHF01GP511XB50 | U1 CNDS TRANS PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C10GHF01GP511XB61 | U1 CNDS TRANS PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C10GHF01GP511XB62 | U1 CNDS TRANS PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C10GHF01GP511XB69 | U1 CNDS TRANS PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C10GHF01GP511XB78 | U1 CNDS TRANS PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C10GHF01GP511XQ01 | U1 CNDS TRANS PP B AMP | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#1) | MCB | TC1-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHC01QN001XB62 | U2 CNDS STR TK INL CV-REMOTE TRIP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C20GHC01QN001XG01 | U2 CNDS STR TK INL CV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C20GHC01QN001XG02 | U2 CNDS STR TK INL CV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C20GHC01QN001XQ02 | U2 CNDS STR TK INL CV-ZT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C20GHC01QN001XQ23 | U2 CNDS STR TK INL CV-PY | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C20GHF01BF301XB27 | U2 CNDS TRANS PP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 120 | m3/hr | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GHF01BF301XQ01 | U2 CNDS TRANS PP OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 120 | m3/hr | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GHF01BL001XG01 | U2 CNDS STR TK LSH | D-DI | 24VDC | S | - | 13500 | - | - | mm | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C20GHF01BL001XG03 | U2 CNDS STR TK LSHH | D-DI | 24VDC | S | 14250 | - | - | - | mm | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C20GHF01BL001XG52 | U2 CNDS STR TK LSL | D-DI | 24VDC | S | - | - | 1500 | - | mm | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C20GHF01BL001XG54 | U2 CNDS STR TK LSLL | D-DI | 24VDC | S | - | - | - | 750 | mm | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C20GHF01BL301XQ01 | U2 CNDS STR TK LIT | D-AI | 4-20mA | S | 14250 | 13500 | 1500 | 750 | mm | NO | YES | - | - | - | 0 | 14805 | mmH2O | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C20GHF01BP301XQ01 | U2 CNDS TRANS PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C20GHF01BP302XQ01 | U2 CNDS TRANS PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C20GHF01BP303XQ01 | U2 CNDS TRANS PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.708 | 0.671 | MPaG | NO | YES | - | - | - | 0 | 1.49 | MPaG | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C20GHF01BT301XQ01 | U2 CNDS TRANS PP OUTL TIT | D-AI | 4-20mA | S | - | 28 | - | - | ℃ | NO | YES | - | - | - | 0 | 100 | ℃ | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C20GHF01GP501XB01 | U2 CNDS TRANS PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHF01GP501XB49 | U2 CNDS TRANS PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHF01GP501XB50 | U2 CNDS TRANS PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHF01GP501XB61 | U2 CNDS TRANS PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C20GHF01GP501XB62 | U2 CNDS TRANS PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C20GHF01GP501XB69 | U2 CNDS TRANS PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C20GHF01GP501XB78 | U2 CNDS TRANS PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHF01GP501XQ01 | U2 CNDS TRANS PP A AMP | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHF01GP511XB01 | U2 CNDS TRANS PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHF01GP511XB49 | U2 CNDS TRANS PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHF01GP511XB50 | U2 CNDS TRANS PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHF01GP511XB61 | U2 CNDS TRANS PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C20GHF01GP511XB62 | U2 CNDS TRANS PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C20GHF01GP511XB69 | U2 CNDS TRANS PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | DCDAS | EMCC | - | - | -
=C20GHF01GP511XB78 | U2 CNDS TRANS PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C20GHF01GP511XQ01 | U2 CNDS TRANS PP B AMP | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | CONDENSATE MAKE-UP SYSTEM (CC#2) | MCB | TC2-1-KDM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XVA01BF302XQ01 | RAINWTR RECV BSN FOR ST OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 20 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | HOLD | TC0-1-CMM02-D6002 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XVA01BF303XQ01 | RAINWTR RECV BSN FOR DWTS OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 20 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | HOLD | TC0-1-CMM02-D6002 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XVA01BF304XQ01 | RAINWTR RECV BSN FOR GT OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 20 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | HOLD | TC0-1-CMM02-D6003 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XVA01BF305XQ01 | RAINWTR RECV BSN FOR AWWTS & WWTS OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 20 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | HOLD | TC0-1-CMM02-D6003 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF301XB27 | DEMIN WTR STG TK A OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | 0 | 2500 | mmH2O | 0 | 745 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF301XQ01 | DEMIN WTR STG TK A OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2500 | mmH2O | 0 | 745 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF302XB27 | DEMIN WTR STG TK B OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | 0 | 2500 | mmH2O | 0 | 745 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF302XQ01 | DEMIN WTR STG TK B OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2500 | mmH2O | 0 | 745 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF303XB27 | DEMIN WTR TRANS PP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | 0 | 2500 | mmH2O | 0 | 490 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF303XQ01 | DEMIN WTR TRANS PP OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2500 | mmH2O | 0 | 490 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BL001XG01 | DEMIN WTR STG TK A LSH | D-DI | 24VDC | S | - | 18000 | - | - | mm | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GHC01BL001XG03 | DEMIN WTR STG TK A LSHH | D-DI | 24VDC | S | 19000 | - | - | - | mm | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GHC01BL001XG52 | DEMIN WTR STG TK A LSL | D-DI | 24VDC | S | - | - | 2000 | - | mm | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GHC01BL001XG54 | DEMIN WTR STG TK A LSLL | D-DI | 24VDC | S | - | - | - | 1000 | mm | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GHC01BL002XG01 | DEMIN WTR STG TK B LSH | D-DI | 24VDC | S | - | 18000 | - | - | mm | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GHC01BL002XG03 | DEMIN WTR STG TK B LSHH | D-DI | 24VDC | S | 19000 | - | - | - | mm | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GHC01BL002XG52 | DEMIN WTR STG TK B LSL | D-DI | 24VDC | S | - | - | 2000 | - | mm | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GHC01BL002XG54 | DEMIN WTR STG TK B LSLL | D-DI | 24VDC | S | - | - | - | 1000 | mm | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GHC01BL301XQ01 | DEMIN WTR STG TK A LIT | D-AI | 4-20mA | S | 19000 | 18000 | 2000 | 1000 | mm | NO | YES | - | - | - | 0 | 19790 | mmH2O | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BL302XQ01 | DEMIN WTR STG TK B LIT | D-AI | 4-20mA | S | 19000 | 18000 | 2000 | 1000 | mm | NO | YES | - | - | - | 0 | 19790 | mmH2O | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BP301XQ01 | DEMIN WTR TRANS PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BP302XQ01 | DEMIN WTR TRANS PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BP303XQ01 | DEMIN WTR TRANS PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.865 | - | MPaG | NO | YES | - | - | - | 0 | 1.822 | MPaG | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01GP501XB01 | DEMIN WTR TRANS PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01GP501XB47 | DEMIN WTR TRANS PP A SVC POSN | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01GP501XB49 | DEMIN WTR TRANS PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01GP501XB61 | DEMIN WTR TRANS PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | DCDAS | PC | - | - | -
=C00GHC01GP501XB62 | DEMIN WTR TRANS PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | DCDAS | PC | - | - | -
=C00GHC01GP501XB69 | DEMIN WTR TRANS PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | DCDAS | PC | - | - | -
=C00GHC01GP501XB74 | DEMIN WTR TRANS PP A READY | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01GP501XB78 | DEMIN WTR TRANS PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01GP511XB01 | DEMIN WTR TRANS PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01GP511XB47 | DEMIN WTR TRANS PP B SVC POSN | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01GP511XB49 | DEMIN WTR TRANS PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01GP511XB61 | DEMIN WTR TRANS PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | DCDAS | MCC | - | - | -
=C00GHC01GP511XB62 | DEMIN WTR TRANS PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | DCDAS | MCC | - | - | -
=C00GHC01GP511XB69 | DEMIN WTR TRANS PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | DCDAS | MCC | - | - | -
=C00GHC01GP511XB74 | DEMIN WTR TRANS PP B READY | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01GP511XB78 | DEMIN WTR TRANS PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | - | PC | DCDAS | - | - | -
=C00GHC01QM061XB62 | DEMIN WTR STG TK A OUTL XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GHC01QM061XG01 | DEMIN WTR STG TK A OUTL XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GHC01QM061XG02 | DEMIN WTR STG TK A OUTL XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GHC01QM062XB62 | DEMIN WTR STG TK B OUTL XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GHC01QM062XG01 | DEMIN WTR STG TK B OUTL XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GHC01QM062XG02 | DEMIN WTR STG TK B OUTL XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6101 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GHC01BF304XB27 | EMRG MAKEUP PP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 180 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF304XQ01 | EMRG MAKEUP PP OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 180 | m3/hr | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BP304XQ01 | EMRG MAKEUP PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BP305XQ01 | EMRG MAKEUP PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BP306XQ01 | EMRG MAKEUP PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.714 | - | MPaG | NO | YES | - | - | - | 0 | 1.504 | MPaG | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01GP502XB01 | EMRG MAKEUP PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00GHC01GP502XB47 | EMRG MAKEUP PP A SVC POSN | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00GHC01GP502XB49 | EMRG MAKEUP PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00GHC01GP502XB61 | EMRG MAKEUP PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | DCDAS | PC | - | - | -
=C00GHC01GP502XB62 | EMRG MAKEUP PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | DCDAS | PC | - | - | -
=C00GHC01GP502XB69 | EMRG MAKEUP PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | DCDAS | PC | - | - | -
=C00GHC01GP502XB74 | EMRG MAKEUP PP A READY | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00GHC01GP502XB78 | EMRG MAKEUP PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00GHC01GP512XB01 | EMRG MAKEUP PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00GHC01GP512XB47 | EMRG MAKEUP PP B SVC POSN | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00GHC01GP512XB49 | EMRG MAKEUP PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00GHC01GP512XB61 | EMRG MAKEUP PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | DCDAS | PC | - | - | -
=C00GHC01GP512XB62 | EMRG MAKEUP PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | DCDAS | PC | - | - | -
=C00GHC01GP512XB69 | EMRG MAKEUP PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | DCDAS | PC | - | - | -
=C00GHC01GP512XB74 | EMRG MAKEUP PP B READY | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00GHC01GP512XB78 | EMRG MAKEUP PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | DEMINERALIZED WATER TRANSFER SYSTEM (COMMON) | DWT | TC0-1-KDM02-D6102 | - | PC | DCDAS | - | - | -
=C00XGC07BP301XQ01 | FIRE MAIN HDR TO CABLE TUNL #1 PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR CABLE TUNNEL | TUNL1 | TC0-1-FFD02-D5007 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGC07BP302XQ01 | FIRE MAIN HDR TO CABLE TUNL #2 PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR CABLE TUNNEL | TUNL1 | TC0-1-FFD02-D5007 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGC07BP303XQ01 | FIRE MAIN HDR TO CABLE TUNL #3 & #4 PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR CABLE TUNNEL | TUNL1 | TC0-1-FFD02-D5007 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGC08BP301XQ01 | FIRE MAIN HDR TO CABLE TUNL #5 & #6 PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR CABLE TUNNEL | TUNL1 | TC0-1-FFD02-D5008 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGC09BP301XQ01 | FIRE MAIN HDR TO CABLE TUNL #7 & #8 PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR CABLE TUNNEL | TUNL1 | TC0-1-FFD02-D5009 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGC10BP301XQ01 | FIRE MAIN HDR TO CABLE TUNL #9 & #10 PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR CABLE TUNNEL | TUNL1 | TC0-1-FFD02-D5010 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGC11BP301XQ01 | FIRE MAIN HDR TO CABLE TUNL #11 & #12 PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR CABLE TUNNEL | TUNL1 | TC0-1-FFD02-D5011 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BF301XQ01 | TO FIRE MAIN LOOP FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2500 | mmH2O | 0 | 1550 | m3/hr | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BP305XQ01 | TO FIRE MAIN LOOP PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 2.46 | MPaG | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BP311XQ01 | JOCKEY PP INL STR PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.02 | MPa | 0 | 0.02 | MPa | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BP321XQ01 | FIRE PP INL STR PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.02 | MPa | 0 | 0.02 | MPa | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BP331XQ01 | FIRE PP INL STR PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.02 | MPa | 0 | 0.02 | MPa | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT321XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT322XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT323XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT324XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT325XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT326XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT327XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT328XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT329XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT330XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT331XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT332XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03BT333XQ01 | FIRE PP TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 150 | ℃ | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00XGA03QM081XB01 | TO U9 & U10 EX FIRE PROT SYS MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XGA03QM081XB02 | TO U9 & U10 EX FIRE PROT SYS MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XGA03QM081XB20 | TO U9 & U10 EX FIRE PROT SYS MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XGA03QM081XB49 | TO U9 & U10 EX FIRE PROT SYS MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00XGA03QM081XB50 | TO U9 & U10 EX FIRE PROT SYS MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00XGA03QM081XB61 | TO U9 & U10 EX FIRE PROT SYS MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00XGA03QM081XB62 | TO U9 & U10 EX FIRE PROT SYS MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00XGA03QM081XB63 | TO U9 & U10 EX FIRE PROT SYS MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XGA03QM081XB64 | TO U9 & U10 EX FIRE PROT SYS MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XGA03QM081XB87 | TO U9 & U10 EX FIRE PROT SYS MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XGA03QM081XB88 | TO U9 & U10 EX FIRE PROT SYS MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XGA03QM081XG33 | TO U9 & U10 EX FIRE PROT SYS MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XGA03QM081XG34 | TO U9 & U10 EX FIRE PROT SYS MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XGA03UH111XB01 | JOCKEY PUMP CTRLR PUMP RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=C00XGA03UH111XB74 | JOCKEY PP CTRLR PWR AVAIL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=C00XGA03UH121XB01 | FIRE PP CTRLR RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=C00XGA03UH121XB40 | FIRE PP CTRLR CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=C00XGA03UH121XB74 | FIRE PP CTRLR PWR AVAIL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=C00XGA03UH131XB01 | FIRE PP CTRLR DIESEL ENGINE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=C00XGA03UH131XB40 | FIRE PP CTRLR CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=C00XGA03UH131XB48 | FIRE PP CTRLR ENGINE TROUBLE ALM | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=C00XGA03UH131XB78 | FIRE PP CTRLR NOT IN AUTO POSITION | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=C00XGA03UH131XD78 | FIRE PUMP CTRLR NOT IN AUTO POSITION | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | FIRE FIGHTING SYSTEM P&ID FOR FIRE WATER PUMP | RFW | TC0-1-FFD02-D5003 | - | FAP | DCDAS | - | - | -
=G11XGC04BP301XQ01 | FIRE MAIN HDR TO U1 GT1 XFMR PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR GT TRANSFORMERS | GT1 | TC0-1-FFD02-D5004 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G12XGC04BP301XQ01 | FIRE MAIN HDR TO U1 GT2 XFMR PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR GT TRANSFORMERS | GT1 | TC0-1-FFD02-D5004 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G21XGC05BP301XQ01 | FIRE MAIN HDR TO U2 GT1 XFMR PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR GT TRANSFORMERS | GT2 | TC0-1-FFD02-D5005 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G22XGC05BP301XQ01 | FIRE MAIN HDR TO U2 GT2 XFMR PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR GT TRANSFORMERS | GT2 | TC0-1-FFD02-D5005 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G11XGA11BP301XQ01 | FIRE MAIN HDR TO U1 GT1 BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 1 GAS TURBINE BLD. | GT1 | TC1-1-FFD02-D5001 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G12XGA11BP301XQ01 | FIRE MAIN HDR TO U1 GT2 BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 1 GAS TURBINE BLD. | GT1 | TC1-1-FFD02-D5001 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G21XGA21BP301XQ01 | FIRE MAIN HDR TO U2 GT1 BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 1 GAS TURBINE BLD. | GT2 | TC2-1-FFD02-D5001 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G22XGA21BP301XQ01 | FIRE MAIN HDR TO U2 GT2 BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 1 GAS TURBINE BLD. | GT2 | TC2-1-FFD02-D5001 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G11XGA13BP301XQ01 | FIRE MAIN HDR TO U1 HRSG1 BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 1 HRSG BLD. | GT1 | TC1-1-FFD02-D5003 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G12XGA13BP301XQ01 | FIRE MAIN HDR TO U1 HRSG2 BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 1 HRSG BLD. | GT1 | TC1-1-FFD02-D5003 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=S10XGA14BP301XQ01 | FIRE MAIN HDR TO U1 ST BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 1 STEAM TURBINE BLD. | ST1 | TC1-1-FFD02-D5004 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G21XGA23BP301XQ01 | FIRE MAIN HDR TO U2 HRSG1 BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 2 HRSG BLD. | GT2 | TC2-1-FFD02-D5003 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=G22XGA23BP301XQ01 | FIRE MAIN HDR TO U2 HRSG2 BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 2 HRSG BLD. | GT2 | TC2-1-FFD02-D5003 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=S20XGA24BP301XQ01 | FIRE MAIN HDR TO U2 ST BLD SPR & HYD SYS PDIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 0.1 | MPa | 0 | 0.1 | MPa | FIRE FIGHTING SYSTEM P&ID FOR UNIT 2 STEAM TURBINE BLD. | ST2 | TC2-1-FFD02-D5004 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C10GHC01QN002XB62 | U1 GT SPY WTR TK INL CV-REMOTE TRIP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C10GHC01QN002XG01 | U1 GT SPY WTR TK INL CV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C10GHC01QN002XG02 | U1 GT SPY WTR TK INL CV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C10GHC01QN002XQ02 | U1 GT SPY WTR TK INL CV-ZT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C10GHC01QN002XQ23 | U1 GT SPY WTR TK INL CV-PY | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C10GHE01BF301XB27 | U1 GT SPY WTR TRANS PP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GHE01BF301XQ01 | U1 GT SPY WTR TRANS PP OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GHE01BL001XG01 | U1 GT SPY WTR TK LSH | D-DI | 24VDC | S | - | 5400 | - | - | mm | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C10GHE01BL001XG03 | U1 GT SPY WTR TK LSHH | D-DI | 24VDC | S | 5700 | - | - | - | mm | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C10GHE01BL001XG52 | U1 GT SPY WTR TK LSL | D-DI | 24VDC | S | - | - | 600 | - | mm | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C10GHE01BL001XG54 | U1 GT SPY WTR TK LSLL | D-DI | 24VDC | S | - | - | - | 300 | mm | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C10GHE01BL301XQ01 | U1 GT SPY WTR TK LIT | D-AI | 4-20mA | S | 5700 | 5400 | 600 | 300 | mm | NO | YES | - | - | - | 0 | 5832 | mmH2O | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C10GHE01BP301XQ01 | U1 GT SPY WTR TRANS PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C10GHE01BP302XQ01 | U1 GT SPY WTR TRANS PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C10GHE01BP303XQ01 | U1 GT SPY WTR TRANS PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.532 | - | MPaG | NO | YES | - | - | - | 0 | 1.12 | MPaG | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C10GHE01GP501XB01 | U1 GT SPY WTR TRANS PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C10GHE01GP501XB49 | U1 GT SPY WTR TRANS PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C10GHE01GP501XB50 | U1 GT SPY WTR TRANS PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C10GHE01GP501XB61 | U1 GT SPY WTR TRANS PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C10GHE01GP501XB62 | U1 GT SPY WTR TRANS PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C10GHE01GP501XB69 | U1 GT SPY WTR TRANS PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C10GHE01GP501XB78 | U1 GT SPY WTR TRANS PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C10GHE01GP511XB01 | U1 GT SPY WTR TRANS PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C10GHE01GP511XB49 | U1 GT SPY WTR TRANS PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C10GHE01GP511XB50 | U1 GT SPY WTR TRANS PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C10GHE01GP511XB61 | U1 GT SPY WTR TRANS PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C10GHE01GP511XB62 | U1 GT SPY WTR TRANS PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C10GHE01GP511XB69 | U1 GT SPY WTR TRANS PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C10GHE01GP511XB78 | U1 GT SPY WTR TRANS PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C10GHE01QM082XB01 | U1 GT SPY WTR TRANS PP A OUTL MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM082XB02 | U1 GT SPY WTR TRANS PP A OUTL MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM082XB20 | U1 GT SPY WTR TRANS PP A OUTL MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM082XB49 | U1 GT SPY WTR TRANS PP A OUTL MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C10GHE01QM082XB50 | U1 GT SPY WTR TRANS PP A OUTL MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C10GHE01QM082XB61 | U1 GT SPY WTR TRANS PP A OUTL MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C10GHE01QM082XB62 | U1 GT SPY WTR TRANS PP A OUTL MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C10GHE01QM082XB63 | U1 GT SPY WTR TRANS PP A OUTL MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10GHE01QM082XB64 | U1 GT SPY WTR TRANS PP A OUTL MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10GHE01QM082XB87 | U1 GT SPY WTR TRANS PP A OUTL MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM082XB88 | U1 GT SPY WTR TRANS PP A OUTL MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM082XG33 | U1 GT SPY WTR TRANS PP A OUTL MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM082XG34 | U1 GT SPY WTR TRANS PP A OUTL MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM083XB01 | U1 GT SPY WTR TRANS PP B OUTL MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM083XB02 | U1 GT SPY WTR TRANS PP B OUTL MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM083XB20 | U1 GT SPY WTR TRANS PP B OUTL MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM083XB49 | U1 GT SPY WTR TRANS PP B OUTL MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C10GHE01QM083XB50 | U1 GT SPY WTR TRANS PP B OUTL MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C10GHE01QM083XB61 | U1 GT SPY WTR TRANS PP B OUTL MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C10GHE01QM083XB62 | U1 GT SPY WTR TRANS PP B OUTL MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C10GHE01QM083XB63 | U1 GT SPY WTR TRANS PP B OUTL MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10GHE01QM083XB64 | U1 GT SPY WTR TRANS PP B OUTL MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C10GHE01QM083XB87 | U1 GT SPY WTR TRANS PP B OUTL MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM083XB88 | U1 GT SPY WTR TRANS PP B OUTL MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM083XG33 | U1 GT SPY WTR TRANS PP B OUTL MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GHE01QM083XG34 | U1 GT SPY WTR TRANS PP B OUTL MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#1) | DWT | TC1-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHC01QN002XB62 | U2 GT SPY WTR TK INL CV-REMOTE TRIP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C20GHC01QN002XG01 | U2 GT SPY WTR TK INL CV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C20GHC01QN002XG02 | U2 GT SPY WTR TK INL CV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C20GHC01QN002XQ02 | U2 GT SPY WTR TK INL CV-ZT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C20GHC01QN002XQ23 | U2 GT SPY WTR TK INL CV-PY | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C20GHE01BF301XB27 | U2 GT SPY WTR TRANS PP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GHE01BF301XQ01 | U2 GT SPY WTR TRANS PP OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GHE01BL001XG01 | U2 GT SPY WTR TK LSH | D-DI | 24VDC | S | - | 5400 | - | - | mm | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C20GHE01BL001XG03 | U2 GT SPY WTR TK LSHH | D-DI | 24VDC | S | 5700 | - | - | - | mm | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C20GHE01BL001XG52 | U2 GT SPY WTR TK LSL | D-DI | 24VDC | S | - | - | 600 | - | mm | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C20GHE01BL001XG54 | U2 GT SPY WTR TK LSLL | D-DI | 24VDC | S | - | - | - | 300 | mm | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C20GHE01BL301XQ01 | U2 GT SPY WTR TK LIT | D-AI | 4-20mA | S | 5700 | 5400 | 600 | 300 | mm | NO | YES | - | - | - | 0 | 5832 | mmH2O | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C20GHE01BP301XQ01 | U2 GT SPY WTR TRANS PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C20GHE01BP302XQ01 | U2 GT SPY WTR TRANS PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C20GHE01BP303XQ01 | U2 GT SPY WTR TRANS PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.532 | - | MPaG | NO | YES | - | - | - | 0 | 1.12 | MPaG | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C20GHE01GP501XB01 | U2 GT SPY WTR TRANS PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C20GHE01GP501XB49 | U2 GT SPY WTR TRANS PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C20GHE01GP501XB50 | U2 GT SPY WTR TRANS PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C20GHE01GP501XB61 | U2 GT SPY WTR TRANS PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C20GHE01GP501XB62 | U2 GT SPY WTR TRANS PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C20GHE01GP501XB69 | U2 GT SPY WTR TRANS PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C20GHE01GP501XB78 | U2 GT SPY WTR TRANS PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C20GHE01GP511XB01 | U2 GT SPY WTR TRANS PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C20GHE01GP511XB49 | U2 GT SPY WTR TRANS PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C20GHE01GP511XB50 | U2 GT SPY WTR TRANS PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C20GHE01GP511XB61 | U2 GT SPY WTR TRANS PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C20GHE01GP511XB62 | U2 GT SPY WTR TRANS PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C20GHE01GP511XB69 | U2 GT SPY WTR TRANS PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | DCDAS | MCC | - | - | -
=C20GHE01GP511XB78 | U2 GT SPY WTR TRANS PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | - | MCC | DCDAS | - | - | -
=C20GHE01QM082XB01 | U2 GT SPY WTR TRANS PP A OUTL MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM082XB02 | U2 GT SPY WTR TRANS PP A OUTL MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM082XB20 | U2 GT SPY WTR TRANS PP A OUTL MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM082XB49 | U2 GT SPY WTR TRANS PP A OUTL MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C20GHE01QM082XB50 | U2 GT SPY WTR TRANS PP A OUTL MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C20GHE01QM082XB61 | U2 GT SPY WTR TRANS PP A OUTL MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C20GHE01QM082XB62 | U2 GT SPY WTR TRANS PP A OUTL MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C20GHE01QM082XB63 | U2 GT SPY WTR TRANS PP A OUTL MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20GHE01QM082XB64 | U2 GT SPY WTR TRANS PP A OUTL MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20GHE01QM082XB87 | U2 GT SPY WTR TRANS PP A OUTL MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM082XB88 | U2 GT SPY WTR TRANS PP A OUTL MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM082XG33 | U2 GT SPY WTR TRANS PP A OUTL MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM082XG34 | U2 GT SPY WTR TRANS PP A OUTL MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM083XB01 | U2 GT SPY WTR TRANS PP B OUTL MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM083XB02 | U2 GT SPY WTR TRANS PP B OUTL MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM083XB20 | U2 GT SPY WTR TRANS PP B OUTL MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM083XB49 | U2 GT SPY WTR TRANS PP B OUTL MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C20GHE01QM083XB50 | U2 GT SPY WTR TRANS PP B OUTL MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C20GHE01QM083XB61 | U2 GT SPY WTR TRANS PP B OUTL MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C20GHE01QM083XB62 | U2 GT SPY WTR TRANS PP B OUTL MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C20GHE01QM083XB63 | U2 GT SPY WTR TRANS PP B OUTL MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20GHE01QM083XB64 | U2 GT SPY WTR TRANS PP B OUTL MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C20GHE01QM083XB87 | U2 GT SPY WTR TRANS PP B OUTL MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM083XB88 | U2 GT SPY WTR TRANS PP B OUTL MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM083XG33 | U2 GT SPY WTR TRANS PP B OUTL MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C20GHE01QM083XG34 | U2 GT SPY WTR TRANS PP B OUTL MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | GAS TURBINE SPRAY WATER SYSTEM (CC#2) | DWT | TC2-1-KDM02-D6301 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10XAA51BT101XQ01 | CC#1 GT_GT ROOM TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA51BT102XQ01 | CC#1 GT_GT ROOM - SPARE TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA51GQ401XB01 | CC#1 GT_FAN-401 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ401XB49 | CC#1 GT_FAN-401 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ401XB50 | CC#1 GT_FAN-401 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ402XB01 | CC#1 GT_FAN-402 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ402XB49 | CC#1 GT_FAN-402 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ402XB50 | CC#1 GT_FAN-402 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ403XB01 | CC#1 GT_FAN-403 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ403XB49 | CC#1 GT_FAN-403 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ403XB50 | CC#1 GT_FAN-403 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ404XB01 | CC#1 GT_FAN-404 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ404XB49 | CC#1 GT_FAN-404 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ404XB50 | CC#1 GT_FAN-404 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ405XB01 | CC#1 GT_FAN-405 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ405XB49 | CC#1 GT_FAN-405 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ405XB50 | CC#1 GT_FAN-405 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ406XB01 | CC#1 GT_FAN-406 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ406XB49 | CC#1 GT_FAN-406 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51GQ406XB50 | CC#1 GT_FAN-406 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51SP101XB01 | CC#1 GT_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51SP101XB49 | CC#1 GT_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51SP101XB50 | CC#1 GT_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51SP102XB01 | CC#1 GT_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51SP102XB49 | CC#1 GT_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA51SP102XB50 | CC#1 GT_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA52BM101XQ01 | CC#1 ST_LABORATORY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52BM102XQ01 | CC#1 ST_ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52BM103XQ01 | CC#1 ST_ST - SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52BT101XQ01 | CC#1 ST_LABORATORY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52BT102XQ01 | CC#1 ST_ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52BT103XQ01 | CC#1 ST_ST ROOM TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52BT104XQ01 | CC#1 ST_ST - SPARE TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC201XB01 | CC#1 ST_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC201XB49 | CC#1 ST_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC201XB50 | CC#1 ST_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC202XB01 | CC#1 ST_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC202XB49 | CC#1 ST_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC202XB50 | CC#1 ST_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC203XB01 | CC#1 ST_IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC203XB49 | CC#1 ST_IAC-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC203XB50 | CC#1 ST_IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC204XB01 | CC#1 ST_IAC-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC204XB49 | CC#1 ST_IAC-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52EC204XB50 | CC#1 ST_IAC-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52SP101XB01 | CC#1 ST_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52SP101XB49 | CC#1 ST_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA52SP101XB50 | CC#1 ST_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53BM101XQ01 | CC#1 HRSG VFD ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53BM102XQ01 | CC#1 HRSG ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53BM103XQ01 | CC#1 HRSG - SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53BT101XQ01 | CC#1 HRSG VFD ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53BT102XQ01 | CC#1 HRSG ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53BT103XQ01 | CC#1 HRSG BUILDING TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53BT104XQ01 | CC#1 HRSG - SPARE TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC201XB01 | CC#1 HRSG IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC201XB49 | CC#1 HRSG IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC201XB50 | CC#1 HRSG IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC202XB01 | CC#1 HRSG IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC202XB49 | CC#1 HRSG IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC202XB50 | CC#1 HRSG IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC203XB01 | CC#1 HRSG IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC203XB49 | CC#1 HRSG IAC-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC203XB50 | CC#1 HRSG IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC204XB01 | CC#1 HRSG IAC-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC204XB49 | CC#1 HRSG IAC-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC204XB50 | CC#1 HRSG IAC-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC205XB01 | CC#1 HRSG IAC-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC205XB49 | CC#1 HRSG IAC-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53EC205XB50 | CC#1 HRSG IAC-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53SP101XB01 | CC#1 HRSG SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53SP101XB49 | CC#1 HRSG SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA53SP101XB50 | CC#1 HRSG SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BJ101XQ01 | CC#1 GTEB_HVAC FAN-308 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ102XQ01 | CC#1 GTEB_HVAC FAN-309 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ103XQ01 | CC#1 GTEB_HVAC AHU-203 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ104XQ01 | CC#1 GTEB_HVAC AHU-204 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ105XQ01 | CC#1 GTEB_HVAC AHU-205 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ106XQ01 | CC#1 GTEB_HVAC AHU-206 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ107XQ01 | CC#1 GTEB_HVAC AHU-207 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ108XQ01 | CC#1 GTEB_HVAC AHU-208 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ109XQ01 | CC#1 GTEB_HVAC AHU-209 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ110XQ01 | CC#1 GTEB_HVAC AHU-210 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ111XQ01 | CC#1 GTEB_HVAC AHU-211 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ112XQ01 | CC#1 GTEB_HVAC AHU-212 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ113XQ01 | CC#1 GTEB_HVAC AHU-213 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ114XQ01 | CC#1 GTEB_HVAC AHU-214 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ115XQ01 | CC#1 GTEB_HVAC CH-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ116XQ01 | CC#1 GTEB_HVAC CH-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ117XQ01 | CC#1 GTEB_HVAC CHP-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ118XQ01 | CC#1 GTEB_HVAC CHP-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ119XQ01 | CC#1 GTEB_HVAC CWP-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ120XQ01 | CC#1 GTEB_HVAC CWP-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ121XQ01 | CC#1 GTEB_HVAC CT-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ122XQ01 | CC#1 GTEB_HVAC CT-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ123XQ01 | CC#1 GTEB_HVAC ACU-501 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BJ124XQ01 | CC#1 GTEB_HVAC ACU-502 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA55BM101XQ01 | CC#1 GTEB_ELECTRICAL SWITCHGEAR ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BM102XQ01 | CC#1 GTEB_CONTROL PANEL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BM103XQ01 | CC#1 GTEB_BATTERY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BM104XQ01 | CC#1 GTEB_UPS ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BM105XQ01 | CC#1 GTEB_ELECTRONIC EQUIPMENT ROOM HUMIDITY | D-AI | 4-20mA | S | 90 | - | - | 20 | % | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BM106XQ01 | CC#1 GTEB_BATTERY CHARGER ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BM107XQ01 | CC#1 GTEB_5F ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BM108XQ01 | CC#1 GTEB_GTEB1-SPARE 1 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BT101XQ01 | CC#1 GTEB_ELECTRICAL SWITCHGEAR ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BT102XQ01 | CC#1 GTEB_CONTROL PANEL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BT103XQ01 | CC#1 GTEB_BATTERY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BT104XQ01 | CC#1 GTEB_UPS ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BT105XQ01 | CC#1 GTEB_ELECTRONIC EQUIPMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BT106XQ01 | CC#1 GTEB_BATTERY CHARGER ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BT107XQ01 | CC#1 GTEB_5F ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BT108XQ01 | CC#1 GTEB_GTEB1-SPARE 1 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EC101XB01 | CC#1 GTEB_CH-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EC101XB49 | CC#1 GTEB_CH-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EC101XB50 | CC#1 GTEB_CH-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EC102XB01 | CC#1 GTEB_CH-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EC102XB49 | CC#1 GTEB_CH-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EC102XB50 | CC#1 GTEB_CH-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ101XB01 | CC#1 GTEB_CT-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ101XB49 | CC#1 GTEB_CT-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ101XB50 | CC#1 GTEB_CT-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ102XB01 | CC#1 GTEB_CT-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ102XB49 | CC#1 GTEB_CT-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ102XB50 | CC#1 GTEB_CT-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ201XB01 | CC#1 GTEB_AHU-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ201XB49 | CC#1 GTEB_AHU-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ201XB50 | CC#1 GTEB_AHU-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ202XB01 | CC#1 GTEB_AHU-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ202XB49 | CC#1 GTEB_AHU-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ202XB50 | CC#1 GTEB_AHU-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ203XB01 | CC#1 GTEB_AHU-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ203XB49 | CC#1 GTEB_AHU-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ203XB50 | CC#1 GTEB_AHU-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ204XB01 | CC#1 GTEB_AHU-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ204XB49 | CC#1 GTEB_AHU-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ204XB50 | CC#1 GTEB_AHU-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ205XB01 | CC#1 GTEB_AHU-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ205XB49 | CC#1 GTEB_AHU-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ205XB50 | CC#1 GTEB_AHU-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ206XB01 | CC#1 GTEB_AHU-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ206XB49 | CC#1 GTEB_AHU-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ206XB50 | CC#1 GTEB_AHU-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ207XB01 | CC#1 GTEB_AHU-207 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ207XB49 | CC#1 GTEB_AHU-207 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ207XB50 | CC#1 GTEB_AHU-207 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ208XB01 | CC#1 GTEB_AHU-208 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ208XB49 | CC#1 GTEB_AHU-208 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ208XB50 | CC#1 GTEB_AHU-208 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ209XB01 | CC#1 GTEB_AHU-209 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ209XB49 | CC#1 GTEB_AHU-209 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ209XB50 | CC#1 GTEB_AHU-209 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ210XB01 | CC#1 GTEB_AHU-210 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ210XB49 | CC#1 GTEB_AHU-210 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ210XB50 | CC#1 GTEB_AHU-210 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ211XB01 | CC#1 GTEB_AHU-211 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ211XB49 | CC#1 GTEB_AHU-211 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ211XB50 | CC#1 GTEB_AHU-211 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ212XB01 | CC#1 GTEB_AHU-212 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ212XB49 | CC#1 GTEB_AHU-212 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ212XB50 | CC#1 GTEB_AHU-212 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ213XB01 | CC#1 GTEB_AHU-213 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ213XB49 | CC#1 GTEB_AHU-213 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ213XB50 | CC#1 GTEB_AHU-213 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ214XB01 | CC#1 GTEB_AHU-214 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ214XB49 | CC#1 GTEB_AHU-214 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ214XB50 | CC#1 GTEB_AHU-214 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ501XB01 | CC#1 GTEB_ACU-501 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ501XB49 | CC#1 GTEB_ACU-501 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ501XB50 | CC#1 GTEB_ACU-501 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ502XB01 | CC#1 GTEB_ACU-502 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ502XB49 | CC#1 GTEB_ACU-502 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ502XB50 | CC#1 GTEB_ACU-502 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP101XB01 | CC#1 GTEB_CHP-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP101XB49 | CC#1 GTEB_CHP-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP101XB50 | CC#1 GTEB_CHP-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP102XB01 | CC#1 GTEB_CHP-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP102XB49 | CC#1 GTEB_CHP-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP102XB50 | CC#1 GTEB_CHP-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP201XB01 | CC#1 GTEB_CWP-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP201XB49 | CC#1 GTEB_CWP-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP201XB50 | CC#1 GTEB_CWP-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP202XB01 | CC#1 GTEB_CWP-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP202XB49 | CC#1 GTEB_CWP-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55GP202XB50 | CC#1 GTEB_CWP-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP101XB01 | CC#1 GTEB_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP101XB49 | CC#1 GTEB_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP101XB50 | CC#1 GTEB_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP102XB01 | CC#1 GTEB_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP102XB49 | CC#1 GTEB_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP102XB50 | CC#1 GTEB_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP103XB01 | CC#1 GTEB_SPARE-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP103XB49 | CC#1 GTEB_SPARE-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP103XB50 | CC#1 GTEB_SPARE-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP104XB01 | CC#1 GTEB_SPARE-104 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP104XB49 | CC#1 GTEB_SPARE-104 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP104XB50 | CC#1 GTEB_SPARE-104 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP105XB01 | CC#1 GTEB_SPARE-105 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP105XB49 | CC#1 GTEB_SPARE-105 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55SP105XB50 | CC#1 GTEB_SPARE-105 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BJ101XQ01 | CC#1 STEB_HVAC CT-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ102XQ01 | CC#1 STEB_HVAC CT-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ103XQ01 | CC#1 STEB_HVAC CT-103 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ104XQ01 | CC#1 STEB_HVAC CHP-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ105XQ01 | CC#1 STEB_HVAC CHP-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ106XQ01 | CC#1 STEB_HVAC CHP-103 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ107XQ01 | CC#1 STEB_HVAC CWP-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ108XQ01 | CC#1 STEB_HVAC CWP-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ109XQ01 | CC#1 STEB_HVAC CWP-203 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ110XQ01 | CC#1 STEB_HVAC FAN-301 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ111XQ01 | CC#1 STEB_HVAC FAN-302 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ112XQ01 | CC#1 STEB_HVAC AHU-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ113XQ01 | CC#1 STEB_HVAC AHU-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ114XQ01 | CC#1 STEB_HVAC AHU-203 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ115XQ01 | CC#1 STEB_HVAC AHU-206 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ116XQ01 | CC#1 STEB_HVAC AHU-207 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ117XQ01 | CC#1 STEB_HVAC FAN-308 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ118XQ01 | CC#1 STEB_HVAC FAN-309 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ119XQ01 | CC#1 STEB_HVAC AHU-208 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ120XQ01 | CC#1 STEB_HVAC AHU-209 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ121XQ01 | CC#1 STEB_HVAC AHU-210 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ122XQ01 | CC#1 STEB_HVAC AHU-211 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ123XQ01 | CC#1 STEB_HVAC AHU-212 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ124XQ01 | CC#1 STEB_HVAC CT-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ125XQ01 | CC#1 STEB_HVAC CT-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ126XQ01 | CC#1 STEB_HVAC CT-103 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ127XQ01 | CC#1 STEB_HVAC ACU-501 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BJ128XQ01 | CC#1 STEB_HVAC ACU-502 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C10XAA56BM101XQ01 | CC#1 STEB_UPS SYSTEM ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BM102XQ01 | CC#1 STEB_ELECTRICAL SWITCHGEAR & MCC ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BM103XQ01 | CC#1 STEB_CHARGER ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BM104XQ01 | CC#1 STEB_ELECTRONIC EQUIPMENT ROOM HUMIDITY | D-AI | 4-20mA | S | 90 | - | - | 20 | % | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BM105XQ01 | CC#1 STEB_BATTERY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BM106XQ01 | CC#1 STEB_STEB1-SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BT101XQ01 | CC#1 STEB_UPS SYSTEM ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BT102XQ01 | CC#1 STEB_ELECTRICAL SWITCHGEAR & MCC ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BT103XQ01 | CC#1 STEB_CHARGER ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BT104XQ01 | CC#1 STEB_ELECTRONIC EQUIPMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BT105XQ01 | CC#1 STEB_BATTERY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56BT106XQ01 | CC#1 STEB_STEB1-SPARE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EC101XB01 | CC#1 STEB_CH-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EC101XB49 | CC#1 STEB_CH-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EC101XB50 | CC#1 STEB_CH-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EC102XB01 | CC#1 STEB_CH-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EC102XB49 | CC#1 STEB_CH-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EC102XB50 | CC#1 STEB_CH-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EC103XB01 | CC#1 STEB_CH-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EC103XB49 | CC#1 STEB_CH-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EC103XB50 | CC#1 STEB_CH-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ101XB01 | CC#1 STEB_CT-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ101XB49 | CC#1 STEB_CT-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ101XB50 | CC#1 STEB_CT-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ102XB01 | CC#1 STEB_CT-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ102XB49 | CC#1 STEB_CT-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ102XB50 | CC#1 STEB_CT-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ103XB01 | CC#1 STEB_CT-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ103XB49 | CC#1 STEB_CT-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ103XB50 | CC#1 STEB_CT-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ201XB01 | CC#1 STEB_AHU-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ201XB49 | CC#1 STEB_AHU-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ201XB50 | CC#1 STEB_AHU-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ202XB01 | CC#1 STEB_AHU-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ202XB49 | CC#1 STEB_AHU-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ202XB50 | CC#1 STEB_AHU-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ203XB01 | CC#1 STEB_AHU-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ203XB49 | CC#1 STEB_AHU-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ203XB50 | CC#1 STEB_AHU-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ204XB01 | CC#1 STEB_AHU-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ204XB49 | CC#1 STEB_AHU-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ204XB50 | CC#1 STEB_AHU-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ205XB01 | CC#1 STEB_AHU-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ205XB49 | CC#1 STEB_AHU-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ205XB50 | CC#1 STEB_AHU-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ206XB01 | CC#1 STEB_AHU-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ206XB49 | CC#1 STEB_AHU-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ206XB50 | CC#1 STEB_AHU-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ207XB01 | CC#1 STEB_AHU-207 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ207XB49 | CC#1 STEB_AHU-207 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ207XB50 | CC#1 STEB_AHU-207 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ208XB01 | CC#1 STEB_AHU-208 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ208XB49 | CC#1 STEB_AHU-208 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ208XB50 | CC#1 STEB_AHU-208 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ209XB01 | CC#1 STEB_AHU-209 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ209XB49 | CC#1 STEB_AHU-209 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ209XB50 | CC#1 STEB_AHU-209 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ210XB01 | CC#1 STEB_AHU-210 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ210XB49 | CC#1 STEB_AHU-210 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ210XB50 | CC#1 STEB_AHU-210 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ211XB01 | CC#1 STEB_AHU-211 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ211XB49 | CC#1 STEB_AHU-211 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ211XB50 | CC#1 STEB_AHU-211 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ212XB01 | CC#1 STEB_AHU-212 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ212XB49 | CC#1 STEB_AHU-212 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ212XB50 | CC#1 STEB_AHU-212 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ501XB01 | CC#1 STEB_ACU-501 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ501XB49 | CC#1 STEB_ACU-501 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ501XB50 | CC#1 STEB_ACU-501 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ502XB01 | CC#1 STEB_ACU-502 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ502XB49 | CC#1 STEB_ACU-502 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56EQ502XB50 | CC#1 STEB_ACU-502 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP101XB01 | CC#1 STEB_CHP-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP101XB49 | CC#1 STEB_CHP-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP101XB50 | CC#1 STEB_CHP-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP102XB01 | CC#1 STEB_CHP-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP102XB49 | CC#1 STEB_CHP-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP102XB50 | CC#1 STEB_CHP-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP103XB01 | CC#1 STEB_CHP-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP103XB49 | CC#1 STEB_CHP-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP103XB50 | CC#1 STEB_CHP-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP201XB01 | CC#1 STEB_CWP-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP201XB49 | CC#1 STEB_CWP-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP201XB50 | CC#1 STEB_CWP-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP202XB01 | CC#1 STEB_CWP-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP202XB49 | CC#1 STEB_CWP-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP202XB50 | CC#1 STEB_CWP-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP203XB01 | CC#1 STEB_CWP-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP203XB49 | CC#1 STEB_CWP-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56GP203XB50 | CC#1 STEB_CWP-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP101XB01 | CC#1 STEB_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP101XB49 | CC#1 STEB_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP101XB50 | CC#1 STEB_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP102XB01 | CC#1 STEB_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP102XB49 | CC#1 STEB_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP102XB50 | CC#1 STEB_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP103XB01 | CC#1 STEB_SPARE-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP103XB49 | CC#1 STEB_SPARE-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP103XB50 | CC#1 STEB_SPARE-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP104XB01 | CC#1 STEB_SPARE-104 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP104XB49 | CC#1 STEB_SPARE-104 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP104XB50 | CC#1 STEB_SPARE-104 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP105XB01 | CC#1 STEB_SPARE-105 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP105XB49 | CC#1 STEB_SPARE-105 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA56SP105XB50 | CC#1 STEB_SPARE-105 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA51BT101XQ01 | CC#2 GT_GT ROOM TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA51BT102XQ01 | CC#2 GT_GT ROOM - SPARE TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA51GQ401XB01 | CC#2 GT_FAN-401 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ401XB49 | CC#2 GT_FAN-401 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ401XB50 | CC#2 GT_FAN-401 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ402XB01 | CC#2 GT_FAN-402 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ402XB49 | CC#2 GT_FAN-402 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ402XB50 | CC#2 GT_FAN-402 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ403XB01 | CC#2 GT_FAN-403 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ403XB49 | CC#2 GT_FAN-403 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ403XB50 | CC#2 GT_FAN-403 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ404XB01 | CC#2 GT_FAN-404 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ404XB49 | CC#2 GT_FAN-404 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ404XB50 | CC#2 GT_FAN-404 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ405XB01 | CC#2 GT_FAN-405 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ405XB49 | CC#2 GT_FAN-405 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ405XB50 | CC#2 GT_FAN-405 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ406XB01 | CC#2 GT_FAN-406 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ406XB49 | CC#2 GT_FAN-406 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51GQ406XB50 | CC#2 GT_FAN-406 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51SP101XB01 | CC#2 GT_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51SP101XB49 | CC#2 GT_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51SP101XB50 | CC#2 GT_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51SP102XB01 | CC#2 GT_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51SP102XB49 | CC#2 GT_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA51SP102XB50 | CC#2 GT_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA52BM101XQ01 | CC#2 ST_LABORATORY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52BM102XQ01 | CC#2 ST_ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52BM103XQ01 | CC#2 ST_ST - SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52BT101XQ01 | CC#2 ST_LABORATORY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52BT102XQ01 | CC#2 ST_ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52BT103XQ01 | CC#2 ST_ST ROOM TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52BT104XQ01 | CC#2 ST_ST - SPARE TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC201XB01 | CC#2 ST_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC201XB49 | CC#2 ST_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC201XB50 | CC#2 ST_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC202XB01 | CC#2 ST_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC202XB49 | CC#2 ST_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC202XB50 | CC#2 ST_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC203XB01 | CC#2 ST_IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC203XB49 | CC#2 ST_IAC-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC203XB50 | CC#2 ST_IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC204XB01 | CC#2 ST_IAC-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC204XB49 | CC#2 ST_IAC-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52EC204XB50 | CC#2 ST_IAC-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52SP101XB01 | CC#2 ST_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52SP101XB49 | CC#2 ST_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA52SP101XB50 | CC#2 ST_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53BM101XQ01 | CC#2 HRSG VFD ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53BM102XQ01 | CC#2 HRSG ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53BM103XQ01 | CC#2 HRSG1_HRSG - SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53BT101XQ01 | CC#2 HRSG VFD ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53BT102XQ01 | CC#2 HRSG ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53BT103XQ01 | CC#2 HRSG BUILDING TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53BT104XQ01 | CC#2 HRSG1_HRSG - SPARE TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC201XB01 | CC#2 HRSG IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC201XB49 | CC#2 HRSG IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC201XB50 | CC#2 HRSG IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC202XB01 | CC#2 HRSG IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC202XB49 | CC#2 HRSG IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC202XB50 | CC#2 HRSG IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC203XB01 | CC#2 HRSG IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC203XB49 | CC#2 HRSG IAC-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC203XB50 | CC#2 HRSG IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC204XB01 | CC#2 HRSG IAC-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC204XB49 | CC#2 HRSG IAC-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC204XB50 | CC#2 HRSG IAC-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC205XB01 | CC#2 HRSG IAC-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC205XB49 | CC#2 HRSG IAC-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53EC205XB50 | CC#2 HRSG IAC-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53SP101XB01 | CC#2 HRSG SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53SP101XB49 | CC#2 HRSG SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA53SP101XB50 | CC#2 HRSG SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | HRSG2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BJ101XQ01 | CC#2 GTEB_HVAC FAN-308 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ102XQ01 | CC#2 GTEB_HVAC FAN-309 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ103XQ01 | CC#2 GTEB_HVAC AHU-203 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ104XQ01 | CC#2 GTEB_HVAC AHU-204 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ105XQ01 | CC#2 GTEB_HVAC AHU-205 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ106XQ01 | CC#2 GTEB_HVAC AHU-206 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ107XQ01 | CC#2 GTEB_HVAC AHU-207 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ108XQ01 | CC#2 GTEB_HVAC AHU-208 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ109XQ01 | CC#2 GTEB_HVAC AHU-209 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ110XQ01 | CC#2 GTEB_HVAC AHU-210 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ111XQ01 | CC#2 GTEB_HVAC AHU-211 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ112XQ01 | CC#2 GTEB_HVAC AHU-212 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ113XQ01 | CC#2 GTEB_HVAC AHU-213 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ114XQ01 | CC#2 GTEB_HVAC AHU-214 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ115XQ01 | CC#2 GTEB_HVAC CH-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ116XQ01 | CC#2 GTEB_HVAC CH-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ117XQ01 | CC#2 GTEB_HVAC CHP-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ118XQ01 | CC#2 GTEB_HVAC CHP-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ119XQ01 | CC#2 GTEB_HVAC CWP-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ120XQ01 | CC#2 GTEB_HVAC CWP-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ121XQ01 | CC#2 GTEB_HVAC CT-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ122XQ01 | CC#2 GTEB_HVAC CT-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ123XQ01 | CC#2 GTEB_HVAC ACU-501 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BJ124XQ01 | CC#2 GTEB_HVAC ACU-502 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA55BM101XQ01 | CC#2 GTEB_ELECTRICAL SWITCHGEAR ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BM102XQ01 | CC#2 GTEB_CONTROL PANEL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BM103XQ01 | CC#2 GTEB_BATTERY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BM104XQ01 | CC#2 GTEB_UPS ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BM105XQ01 | CC#2 GTEB_ELECTRONIC EQUIPMENT ROOM HUMIDITY | D-AI | 4-20mA | S | 90 | - | - | 20 | % | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BM106XQ01 | CC#2 GTEB_BATTERY CHARGER ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BM107XQ01 | CC#2 GTEB_5F ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BM108XQ01 | CC#2 GTEB_GTEB1-SPARE 1 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BT101XQ01 | CC#2 GTEB_ELECTRICAL SWITCHGEAR ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BT102XQ01 | CC#2 GTEB_CONTROL PANEL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BT103XQ01 | CC#2 GTEB_BATTERY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BT104XQ01 | CC#2 GTEB_UPS ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BT105XQ01 | CC#2 GTEB_ELECTRONIC EQUIPMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BT106XQ01 | CC#2 GTEB_BATTERY CHARGER ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BT107XQ01 | CC#2 GTEB_5F ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BT108XQ01 | CC#2 GTEB_GTEB1-SPARE 1 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EC101XB01 | CC#2 GTEB_CH-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EC101XB49 | CC#2 GTEB_CH-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EC101XB50 | CC#2 GTEB_CH-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EC102XB01 | CC#2 GTEB_CH-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EC102XB49 | CC#2 GTEB_CH-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EC102XB50 | CC#2 GTEB_CH-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ101XB01 | CC#2 GTEB_CT-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ101XB49 | CC#2 GTEB_CT-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ101XB50 | CC#2 GTEB_CT-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ102XB01 | CC#2 GTEB_CT-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ102XB49 | CC#2 GTEB_CT-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ102XB50 | CC#2 GTEB_CT-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ201XB01 | CC#2 GTEB_AHU-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ201XB49 | CC#2 GTEB_AHU-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ201XB50 | CC#2 GTEB_AHU-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ202XB01 | CC#2 GTEB_AHU-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ202XB49 | CC#2 GTEB_AHU-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ202XB50 | CC#2 GTEB_AHU-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ203XB01 | CC#2 GTEB_AHU-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ203XB49 | CC#2 GTEB_AHU-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ203XB50 | CC#2 GTEB_AHU-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ204XB01 | CC#2 GTEB_AHU-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ204XB49 | CC#2 GTEB_AHU-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ204XB50 | CC#2 GTEB_AHU-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ205XB01 | CC#2 GTEB_AHU-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ205XB49 | CC#2 GTEB_AHU-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ205XB50 | CC#2 GTEB_AHU-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ206XB01 | CC#2 GTEB_AHU-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ206XB49 | CC#2 GTEB_AHU-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ206XB50 | CC#2 GTEB_AHU-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ207XB01 | CC#2 GTEB_AHU-207 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ207XB49 | CC#2 GTEB_AHU-207 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ207XB50 | CC#2 GTEB_AHU-207 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ208XB01 | CC#2 GTEB_AHU-208 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ208XB49 | CC#2 GTEB_AHU-208 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ208XB50 | CC#2 GTEB_AHU-208 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ209XB01 | CC#2 GTEB_AHU-209 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ209XB49 | CC#2 GTEB_AHU-209 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ209XB50 | CC#2 GTEB_AHU-209 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ210XB01 | CC#2 GTEB_AHU-210 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ210XB49 | CC#2 GTEB_AHU-210 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ210XB50 | CC#2 GTEB_AHU-210 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ211XB01 | CC#2 GTEB_AHU-211 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ211XB49 | CC#2 GTEB_AHU-211 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ211XB50 | CC#2 GTEB_AHU-211 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ212XB01 | CC#2 GTEB_AHU-212 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ212XB49 | CC#2 GTEB_AHU-212 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ212XB50 | CC#2 GTEB_AHU-212 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ213XB01 | CC#2 GTEB_AHU-213 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ213XB49 | CC#2 GTEB_AHU-213 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ213XB50 | CC#2 GTEB_AHU-213 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ214XB01 | CC#2 GTEB_AHU-214 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ214XB49 | CC#2 GTEB_AHU-214 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ214XB50 | CC#2 GTEB_AHU-214 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ501XB01 | CC#2 GTEB_ACU-501 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ501XB49 | CC#2 GTEB_ACU-501 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ501XB50 | CC#2 GTEB_ACU-501 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ502XB01 | CC#2 GTEB_ACU-502 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ502XB49 | CC#2 GTEB_ACU-502 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ502XB50 | CC#2 GTEB_ACU-502 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP101XB01 | CC#2 GTEB_CHP-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP101XB49 | CC#2 GTEB_CHP-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP101XB50 | CC#2 GTEB_CHP-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP102XB01 | CC#2 GTEB_CHP-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP102XB49 | CC#2 GTEB_CHP-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP102XB50 | CC#2 GTEB_CHP-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP201XB01 | CC#2 GTEB_CWP-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP201XB49 | CC#2 GTEB_CWP-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP201XB50 | CC#2 GTEB_CWP-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP202XB01 | CC#2 GTEB_CWP-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP202XB49 | CC#2 GTEB_CWP-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55GP202XB50 | CC#2 GTEB_CWP-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP101XB01 | CC#2 GTEB_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP101XB49 | CC#2 GTEB_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP101XB50 | CC#2 GTEB_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP102XB01 | CC#2 GTEB_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP102XB49 | CC#2 GTEB_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP102XB50 | CC#2 GTEB_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP103XB01 | CC#2 GTEB_SPARE-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP103XB49 | CC#2 GTEB_SPARE-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP103XB50 | CC#2 GTEB_SPARE-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP104XB01 | CC#2 GTEB_SPARE-104 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP104XB49 | CC#2 GTEB_SPARE-104 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP104XB50 | CC#2 GTEB_SPARE-104 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP105XB01 | CC#2 GTEB_SPARE-105 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP105XB49 | CC#2 GTEB_SPARE-105 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55SP105XB50 | CC#2 GTEB_SPARE-105 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BJ101XQ01 | CC#2 STEB_HVAC CT-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ102XQ01 | CC#2 STEB_HVAC CT-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ103XQ01 | CC#2 STEB_HVAC CT-103 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ104XQ01 | CC#2 STEB_HVAC CHP-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ105XQ01 | CC#2 STEB_HVAC CHP-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ106XQ01 | CC#2 STEB_HVAC CHP-103 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ107XQ01 | CC#2 STEB_HVAC CWP-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ108XQ01 | CC#2 STEB_HVAC CWP-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ109XQ01 | CC#2 STEB_HVAC CWP-203 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ110XQ01 | CC#2 STEB_HVAC FAN-301 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ111XQ01 | CC#2 STEB_HVAC FAN-302 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ112XQ01 | CC#2 STEB_HVAC AHU-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ113XQ01 | CC#2 STEB_HVAC AHU-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ114XQ01 | CC#2 STEB_HVAC AHU-203 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ115XQ01 | CC#2 STEB_HVAC AHU-206 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ116XQ01 | CC#2 STEB_HVAC AHU-207 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ117XQ01 | CC#2 STEB_HVAC FAN-308 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ118XQ01 | CC#2 STEB_HVAC FAN-309 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ119XQ01 | CC#2 STEB_HVAC AHU-208 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ120XQ01 | CC#2 STEB_HVAC AHU-209 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ121XQ01 | CC#2 STEB_HVAC AHU-210 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ122XQ01 | CC#2 STEB_HVAC AHU-211 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ123XQ01 | CC#2 STEB_HVAC AHU-212 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ124XQ01 | CC#2 STEB_HVAC CT-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ125XQ01 | CC#2 STEB_HVAC CT-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ126XQ01 | CC#2 STEB_HVAC CT-103 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ127XQ01 | CC#2 STEB_HVAC ACU-501 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BJ128XQ01 | CC#2 STEB_HVAC ACU-502 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=C20XAA56BM101XQ01 | CC#2 STEB_UPS SYSTEM ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BM102XQ01 | CC#2 STEB_ELECTRICAL SWITCHGEAR & MCC ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BM103XQ01 | CC#2 STEB_CHARGER ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BM104XQ01 | CC#2 STEB_ELECTRONIC EQUIPMENT ROOM HUMIDITY | D-AI | 4-20mA | S | 90 | - | - | 20 | % | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BM105XQ01 | CC#2 STEB_BATTERY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BM106XQ01 | CC#2 STEB_STEB2-SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BT101XQ01 | CC#2 STEB_UPS SYSTEM ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BT102XQ01 | CC#2 STEB_ELECTRICAL SWITCHGEAR & MCC ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BT103XQ01 | CC#2 STEB_CHARGER ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BT104XQ01 | CC#2 STEB_ELECTRONIC EQUIPMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BT105XQ01 | CC#2 STEB_BATTERY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56BT106XQ01 | CC#2 STEB_STEB2-SPARE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EC101XB01 | CC#2 STEB_CH-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EC101XB49 | CC#2 STEB_CH-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EC101XB50 | CC#2 STEB_CH-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EC102XB01 | CC#2 STEB_CH-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EC102XB49 | CC#2 STEB_CH-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EC102XB50 | CC#2 STEB_CH-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EC103XB01 | CC#2 STEB_CH-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EC103XB49 | CC#2 STEB_CH-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EC103XB50 | CC#2 STEB_CH-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ101XB01 | CC#2 STEB_CT-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ101XB49 | CC#2 STEB_CT-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ101XB50 | CC#2 STEB_CT-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ102XB01 | CC#2 STEB_CT-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ102XB49 | CC#2 STEB_CT-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ102XB50 | CC#2 STEB_CT-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ103XB01 | CC#2 STEB_CT-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ103XB49 | CC#2 STEB_CT-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ103XB50 | CC#2 STEB_CT-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ201XB01 | CC#2 STEB_AHU-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ201XB49 | CC#2 STEB_AHU-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ201XB50 | CC#2 STEB_AHU-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ202XB01 | CC#2 STEB_AHU-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ202XB49 | CC#2 STEB_AHU-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ202XB50 | CC#2 STEB_AHU-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ203XB01 | CC#2 STEB_AHU-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ203XB49 | CC#2 STEB_AHU-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ203XB50 | CC#2 STEB_AHU-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ204XB01 | CC#2 STEB_AHU-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ204XB49 | CC#2 STEB_AHU-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ204XB50 | CC#2 STEB_AHU-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ205XB01 | CC#2 STEB_AHU-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ205XB49 | CC#2 STEB_AHU-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ205XB50 | CC#2 STEB_AHU-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ206XB01 | CC#2 STEB_AHU-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ206XB49 | CC#2 STEB_AHU-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ206XB50 | CC#2 STEB_AHU-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ207XB01 | CC#2 STEB_AHU-207 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ207XB49 | CC#2 STEB_AHU-207 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ207XB50 | CC#2 STEB_AHU-207 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ208XB01 | CC#2 STEB_AHU-208 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ208XB49 | CC#2 STEB_AHU-208 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ208XB50 | CC#2 STEB_AHU-208 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ209XB01 | CC#2 STEB_AHU-209 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ209XB49 | CC#2 STEB_AHU-209 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ209XB50 | CC#2 STEB_AHU-209 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ210XB01 | CC#2 STEB_AHU-210 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ210XB49 | CC#2 STEB_AHU-210 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ210XB50 | CC#2 STEB_AHU-210 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ211XB01 | CC#2 STEB_AHU-211 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ211XB49 | CC#2 STEB_AHU-211 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ211XB50 | CC#2 STEB_AHU-211 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ212XB01 | CC#2 STEB_AHU-212 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ212XB49 | CC#2 STEB_AHU-212 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ212XB50 | CC#2 STEB_AHU-212 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ501XB01 | CC#2 STEB_ACU-501 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ501XB49 | CC#2 STEB_ACU-501 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ501XB50 | CC#2 STEB_ACU-501 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ502XB01 | CC#2 STEB_ACU-502 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ502XB49 | CC#2 STEB_ACU-502 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56EQ502XB50 | CC#2 STEB_ACU-502 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP101XB01 | CC#2 STEB_CHP-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP101XB49 | CC#2 STEB_CHP-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP101XB50 | CC#2 STEB_CHP-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP102XB01 | CC#2 STEB_CHP-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP102XB49 | CC#2 STEB_CHP-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP102XB50 | CC#2 STEB_CHP-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP103XB01 | CC#2 STEB_CHP-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP103XB49 | CC#2 STEB_CHP-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP103XB50 | CC#2 STEB_CHP-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP201XB01 | CC#2 STEB_CWP-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP201XB49 | CC#2 STEB_CWP-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP201XB50 | CC#2 STEB_CWP-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP202XB01 | CC#2 STEB_CWP-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP202XB49 | CC#2 STEB_CWP-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP202XB50 | CC#2 STEB_CWP-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP203XB01 | CC#2 STEB_CWP-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP203XB49 | CC#2 STEB_CWP-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56GP203XB50 | CC#2 STEB_CWP-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP101XB01 | CC#2 STEB_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP101XB49 | CC#2 STEB_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP101XB50 | CC#2 STEB_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP102XB01 | CC#2 STEB_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP102XB49 | CC#2 STEB_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP102XB50 | CC#2 STEB_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP103XB01 | CC#2 STEB_SPARE-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP103XB49 | CC#2 STEB_SPARE-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP103XB50 | CC#2 STEB_SPARE-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP104XB01 | CC#2 STEB_SPARE-104 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP104XB49 | CC#2 STEB_SPARE-104 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP104XB50 | CC#2 STEB_SPARE-104 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP105XB01 | CC#2 STEB_SPARE-105 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP105XB49 | CC#2 STEB_SPARE-105 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA56SP105XB50 | CC#2 STEB_SPARE-105 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | ST2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BJ101XQ01 | MCB_HVAC AHU-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ102XQ01 | MCB_HVAC AHU-203 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ103XQ01 | MCB_HVAC AHU-204 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ104XQ01 | MCB_HVAC ACU-501 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ105XQ01 | MCB_HVAC AHU-206 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ106XQ01 | MCB_HVAC AHU-207 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ107XQ01 | MCB_HVAC AHU-209 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ108XQ01 | MCB_HVAC AHU-210 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ109XQ01 | MCB_HVAC FAN-303 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ110XQ01 | MCB_HVAC FAN-304 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ111XQ01 | MCB_HVAC AHU-216 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ112XQ01 | MCB_HVAC AHU-217 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ113XQ01 | MCB_HVAC AHU-218 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ114XQ01 | MCB_HVAC AHU-219 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ115XQ01 | MCB_HVAC AHU-220 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ116XQ01 | MCB_HVAC AHU-221 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ117XQ01 | MCB_HVAC AHU-222 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ118XQ01 | MCB_HVAC AHU-223 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ119XQ01 | MCB_HVAC CH-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ120XQ01 | MCB_HVAC CH-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ121XQ01 | MCB_HVAC CH-103 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ122XQ01 | MCB_HVAC CHP-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ123XQ01 | MCB_HVAC CHP-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ124XQ01 | MCB_HVAC CHP-103 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ125XQ01 | MCB_HVAC CHP-104 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ126XQ01 | MCB_HVAC CHP-105 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ127XQ01 | MCB_HVAC CWP-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ128XQ01 | MCB_HVAC CWP-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ129XQ01 | MCB_HVAC CWP-203 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ130XQ01 | MCB_HVAC CT-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ131XQ01 | MCB_HVAC CT-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ132XQ01 | MCB_HVAC CT-103 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ133XQ01 | MCB_HVAC ACU-502 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BJ134XQ01 | MCB_HVAC ACU-503 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA57BM101XQ01 | MCB_1F SWITCH HUB ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM102XQ01 | MCB_1F PERAM LIBRARY & DATA WAREHOUSE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM103XQ01 | MCB_1F PERAM OFFICE & WORK ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM201XQ01 | MCB_2F PERAM INSTRUMENT ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM202XQ01 | MCB_2F SWITCH HUB ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM203XQ01 | MCB_2F PERAM CONFERENCE ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM204XQ01 | MCB_2F PERAM OFFICE & WORK ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM301XQ01 | MCB_3F PERAM INSTRUMENT ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM302XQ01 | MCB_3F SWITCH HUB ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM303XQ01 | MCB_3F PERAM CONFERENCE ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM304XQ01 | MCB_3F OFFICE (1) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM305XQ01 | MCB_3F OFFICE (2) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM306XQ01 | MCB_3F CONFERENCE ROOM (1) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM307XQ01 | MCB_3F CONFERENCE ROOM (2) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM308XQ01 | MCB_3F PLANT DATA ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM309XQ01 | MCB_3F DUTY OFFICE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM310XQ01 | MCB_3F OFFICE (3) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM401XQ01 | MCB_4F PLANT DATA ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM402XQ01 | MCB_4F OFFICE (4) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM403XQ01 | MCB_4F SWITCH HUB ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM404XQ01 | MCB_4F ENGINEERING ROOM (2) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM405XQ01 | MCB_4F ENGINEERING ROOM (1) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM406XQ01 | MCB_4F TRAINING SIMULATOR MACHINE ROOM (1) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM407XQ01 | MCB_4F TRAINING SIMULATOR MACHINE ROOM (2) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM408XQ01 | MCB_4F CONFERENCE ROOM (3) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM409XQ01 | MCB_4F CONFERENCE ROOM (4) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM501XQ01 | MCB_5F CHARGER ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM502XQ01 | MCB_5F UPS ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM503XQ01 | MCB_5F BATTERY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM504XQ01 | MCB_5F MCC ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM601XQ01 | MCB_6F LOCAL COMPUTER FACILITIES HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM701XQ01 | MCB_7F OFFICE (5) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM702XQ01 | MCB_7F OFFICE (6) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM703XQ01 | MCB_7F SWITCH HUB ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM704XQ01 | MCB_7F COMPUTER (1-1) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM705XQ01 | MCB_7F COMPUTER (1-2) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM706XQ01 | MCB_7F COMPUTER ROOM (2-1) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM707XQ01 | MCB_7F COMPUTER ROOM (2-2) HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM708XQ01 | MCB_7F CENTRAL CONTROL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM801XQ01 | MCB_8F CHILLER & AHU ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM901XQ01 | MCB_MCB-SPARE 1 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM902XQ01 | MCB_MCB-SPARE 2 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM903XQ01 | MCB_MCB-SPARE 3 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM904XQ01 | MCB_MCB-SPARE 4 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM905XQ01 | MCB_MCB-SPARE 5 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM906XQ01 | MCB_MCB-SPARE 6 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM907XQ01 | MCB_MCB-SPARE 7 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BM908XQ01 | MCB_MCB-SPARE 8 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT101XQ01 | MCB_1F SWITCH HUB ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT102XQ01 | MCB_1F PERAM LIBRARY & DATA WAREHOUSE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT103XQ01 | MCB_1F PERAM OFFICE & WORK ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT201XQ01 | MCB_2F PERAM INSTRUMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT202XQ01 | MCB_2F SWITCH HUB ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT203XQ01 | MCB_2F PERAM CONFERENCE ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT204XQ01 | MCB_2F PERAM OFFICE & WORK ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT301XQ01 | MCB_3F PERAM INSTRUMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT302XQ01 | MCB_3F SWITCH HUB ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT303XQ01 | MCB_3F PERAM CONFERENCE ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT304XQ01 | MCB_3F OFFICE (1) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT305XQ01 | MCB_3F OFFICE (2) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT306XQ01 | MCB_3F CONFERENCE ROOM (1) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT307XQ01 | MCB_3F CONFERENCE ROOM (2) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT308XQ01 | MCB_3F PLANT DATA ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT309XQ01 | MCB_3F DUTY OFFICE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT310XQ01 | MCB_3F OFFICE (3) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT401XQ01 | MCB_4F PLANT DATA ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT402XQ01 | MCB_4F OFFICE (4) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT403XQ01 | MCB_4F SWITCH HUB ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT404XQ01 | MCB_4F ENGINEERING ROOM (2) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT405XQ01 | MCB_4F ENGINEERING ROOM (1) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT406XQ01 | MCB_4F TRAINING SIMULATOR MACHINE ROOM (1) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT407XQ01 | MCB_4F TRAINING SIMULATOR MACHINE ROOM (2) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT408XQ01 | MCB_4F CONFERENCE ROOM (3) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT409XQ01 | MCB_4F CONFERENCE ROOM (4) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT501XQ01 | MCB_5F CHARGER ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT502XQ01 | MCB_5F UPS ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT503XQ01 | MCB_5F BATTERY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT504XQ01 | MCB_5F MCC ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT601XQ01 | MCB_6F LOCAL COMPUTER FACILITIES TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT701XQ01 | MCB_7F OFFICE (5) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT702XQ01 | MCB_7F OFFICE (6) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT703XQ01 | MCB_7F SWITCH HUB ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT704XQ01 | MCB_7F COMPUTER ROOM (1-1) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT705XQ01 | MCB_7F COMPUTER ROOM (1-2) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT706XQ01 | MCB_7F COMPUTER ROOM (2-1) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT707XQ01 | MCB_7F COMPUTER ROOM (2-2) TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT708XQ01 | MCB_7F CENTRAL CONTROL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT801XQ01 | MCB_8F CHILLER & AHU ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT901XQ01 | MCB_MCB-SPARE 1 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT902XQ01 | MCB_MCB-SPARE 2 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT903XQ01 | MCB_MCB-SPARE 3 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT904XQ01 | MCB_MCB-SPARE 4 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT905XQ01 | MCB_MCB-SPARE 5 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT906XQ01 | MCB_MCB-SPARE 6 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT907XQ01 | MCB_MCB-SPARE 7 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57BT908XQ01 | MCB_MCB-SPARE 8 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EC101XB01 | MCB_CH-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EC101XB49 | MCB_CH-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EC101XB50 | MCB_CH-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EC102XB01 | MCB_CH-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EC102XB49 | MCB_CH-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EC102XB50 | MCB_CH-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EC103XB01 | MCB_CH-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EC103XB49 | MCB_CH-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EC103XB50 | MCB_CH-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ101XB01 | MCB_CT-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ101XB49 | MCB_CT-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ101XB50 | MCB_CT-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ102XB01 | MCB_CT-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ102XB49 | MCB_CT-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ102XB50 | MCB_CT-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ103XB01 | MCB_CT-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ103XB49 | MCB_CT-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ103XB50 | MCB_CT-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ201XB01 | MCB_PAHU-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ201XB49 | MCB_PAHU-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ201XB50 | MCB_PAHU-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ202XB01 | MCB_AHU-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ202XB49 | MCB_AHU-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ202XB50 | MCB_AHU-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ203XB01 | MCB_AHU-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ203XB49 | MCB_AHU-203 ROOM ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ203XB50 | MCB_AHU-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ204XB01 | MCB_AHU-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ204XB49 | MCB_AHU-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ204XB50 | MCB_AHU-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ205XB01 | MCB_PAHU-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ205XB49 | MCB_PAHU-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ205XB50 | MCB_PAHU-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ206XB01 | MCB_AHU-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ206XB49 | MCB_AHU-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ206XB50 | MCB_AHU-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ207XB01 | MCB_AHU-207 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ207XB49 | MCB_AHU-207 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ207XB50 | MCB_AHU-207 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ208XB01 | MCB_PAHU-208 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ208XB49 | MCB_PAHU-208 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ208XB50 | MCB_PAHU-208 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ209XB01 | MCB_AHU-209 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ209XB49 | MCB_AHU-209 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ209XB50 | MCB_AHU-209 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ210XB01 | MCB_AHU-210 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ210XB49 | MCB_AHU-210 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ210XB50 | MCB_AHU-210 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ211XB01 | MCB_PAHU-211 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ211XB49 | MCB_PAHU-211 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ211XB50 | MCB_PAHU-211 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ212XB01 | MCB_AHU-212 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ212XB49 | MCB_AHU-212 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ212XB50 | MCB_AHU-212 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ213XB01 | MCB_AHU-213 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ213XB49 | MCB_AHU-213 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ213XB50 | MCB_AHU-213 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ214XB01 | MCB_AHU-214 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ214XB49 | MCB_AHU-214 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ214XB50 | MCB_AHU-214 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ215XB01 | MCB_PAHU-215 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ215XB49 | MCB_PAHU-215 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ215XB50 | MCB_PAHU-215 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ216XB01 | MCB_AHU-216 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ216XB49 | MCB_AHU-216 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ216XB50 | MCB_AHU-216 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ217XB01 | MCB_AHU-217 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ217XB49 | MCB_AHU-217 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ217XB50 | MCB_AHU-217 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ218XB01 | MCB_AHU-218 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ218XB49 | MCB_AHU-218 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ218XB50 | MCB_AHU-218 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ219XB01 | MCB_AHU-219 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ219XB49 | MCB_AHU-219 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ219XB50 | MCB_AHU-219 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ220XB01 | MCB_AHU-220 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ220XB49 | MCB_AHU-220 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ220XB50 | MCB_AHU-220 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ221XB01 | MCB_AHU-221 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ221XB49 | MCB_AHU-221 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ221XB50 | MCB_AHU-221 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ222XB01 | MCB_AHU-222 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ222XB49 | MCB_AHU-222 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ222XB50 | MCB_AHU-222 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ223XB01 | MCB_AHU-223 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ223XB49 | MCB_AHU-223 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ223XB50 | MCB_AHU-223 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ501XB01 | MCB_ACU-501 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ501XB49 | MCB_ACU-501 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ501XB50 | MCB_ACU-501 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ502XB01 | MCB_ACU-502 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ502XB49 | MCB_ACU-502 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ502XB50 | MCB_ACU-502 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ503XB01 | MCB_ACU-503 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ503XB49 | MCB_ACU-503 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57EQ503XB50 | MCB_ACU-503 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP101XB01 | MCB_CHP-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP101XB49 | MCB_CHP-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP101XB50 | MCB_CHP-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP102XB01 | MCB_CHP-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP102XB49 | MCB_CHP-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP102XB50 | MCB_CHP-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP103XB01 | MCB_CHP-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP103XB49 | MCB_CHP-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP103XB50 | MCB_CHP-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP104XB01 | MCB_CHP-104 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP104XB49 | MCB_CHP-104 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP104XB50 | MCB_CHP-104 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP105XB01 | MCB_CHP-105 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP105XB49 | MCB_CHP-105 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP105XB50 | MCB_CHP-105 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP201XB01 | MCB_CWP-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP201XB49 | MCB_CWP-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP201XB50 | MCB_CWP-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP202XB01 | MCB_CWP-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP202XB49 | MCB_CWP-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP202XB50 | MCB_CWP-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP203XB01 | MCB_CWP-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP203XB49 | MCB_CWP-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57GP203XB50 | MCB_CWP-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP101XB01 | MCB_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP101XB49 | MCB_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP101XB50 | MCB_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP102XB01 | MCB_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP102XB49 | MCB_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP102XB50 | MCB_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP103XB01 | MCB_SPARE-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP103XB49 | MCB_SPARE-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP103XB50 | MCB_SPARE-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP104XB01 | MCB_SPARE-104 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP104XB49 | MCB_SPARE-104 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP104XB50 | MCB_SPARE-104 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP105XB01 | MCB_SPARE-105 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP105XB49 | MCB_SPARE-105 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP105XB50 | MCB_SPARE-105 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP106XB01 | MCB_SPARE-106 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP106XB49 | MCB_SPARE-106 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP106XB50 | MCB_SPARE-106 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP107XB01 | MCB_SPARE-107 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP107XB49 | MCB_SPARE-107 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP107XB50 | MCB_SPARE-107 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP108XB01 | MCB_SPARE-108 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP108XB49 | MCB_SPARE-108 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA57SP108XB50 | MCB_SPARE-108 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | MCB | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58BM101XQ01 | TIAC_ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58BM102XQ01 | TIAC_TIAC-SPARE ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58BT101XQ01 | TIAC_ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58BT102XQ01 | TIAC_TIAC-SPARE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58EC201XB01 | TIAC_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58EC201XB49 | TIAC_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58EC201XB50 | TIAC_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58EC202XB01 | TIAC_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58EC202XB49 | TIAC_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58EC202XB50 | TIAC_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58EC203XB01 | TIAC_IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58EC203XB49 | TIAC_IAC-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA58EC203XB50 | TIAC_IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59BM101XQ01 | GTMS_ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59BM102XQ01 | GTMS_PV SYSTEM ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59BM103XQ01 | GTMS_MANAGEMENT OFFICE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59BM104XQ01 | GTMS_GTMS-SPARE OFFICE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59BT101XQ01 | GTMS_ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59BT102XQ01 | GTMS_PV SYSTEM ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59BT103XQ01 | GTMS_MANAGEMENT OFFICE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59BT104XQ01 | GTMS_GTMS-SPARE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC201XB01 | GTMS_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC201XB49 | GTMS_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC201XB50 | GTMS_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC202XB01 | GTMS_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC202XB49 | GTMS_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC202XB50 | GTMS_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC203XB01 | GTMS_IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC203XB49 | GTMS_IAC-203 ROOM ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC203XB50 | GTMS_IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC204XB01 | GTMS_IAC-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC204XB49 | GTMS_IAC-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC204XB50 | GTMS_IAC-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC205XB01 | GTMS_IAC-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC205XB49 | GTMS_IAC-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC205XB50 | GTMS_IAC-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC206XB01 | GTMS_IAC-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC206XB49 | GTMS_IAC-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59EC206XB50 | GTMS_IAC-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59SP201XB01 | GTMS_SPARE-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59SP201XB49 | GTMS_SPARE-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59SP201XB50 | GTMS_SPARE-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59SP202XB01 | GTMS_SPARE-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59SP202XB49 | GTMS_SPARE-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA59SP202XB50 | GTMS_SPARE-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BJ101XQ01 | DWTP_HVAC CH-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ102XQ01 | DWTP_HVAC CH-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ103XQ01 | DWTP_HVAC CHP-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ104XQ01 | DWTP_HVAC CHP-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ105XQ01 | DWTP_HVAC CWP-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ106XQ01 | DWTP_HVAC CWP-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ107XQ01 | DWTP_HVAC AHU-208 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ108XQ01 | DWTP_HVAC AHU-209 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ109XQ01 | DWTP_HVAC AHU-210 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ110XQ01 | DWTP_HVAC AHU-211 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ111XQ01 | DWTP_HVAC AHU-212 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ112XQ01 | DWTP_HVAC AHU-213 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ113XQ01 | DWTP_HVAC AHU-214 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ114XQ01 | DWTP_HVAC FAN-303 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ115XQ01 | DWTP_HVAC FAN-304 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ116XQ01 | DWTP_HVAC FAN-305 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ117XQ01 | DWTP_HVAC FAN-306 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ118XQ01 | DWTP_HVAC CT-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ119XQ01 | DWTP_HVAC CT-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BJ120XQ01 | DWTP_HVAC ACU-502 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA60BM101XQ01 | DWTP_LABORATORY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BM102XQ01 | DWTP_ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BM103XQ01 | DWTP_EER HUMIDITY | D-AI | 4-20mA | S | 90 | - | - | 20 | % | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BM104XQ01 | DWTP_OFFICE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BM105XQ01 | DWTP_UPS ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BM106XQ01 | DWTP_CHARGER ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BM107XQ01 | DWTP_BATTERY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BM108XQ01 | DWTP_DWTP-SPARE 1 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BM109XQ01 | DWTP_DWTP-SPARE 2 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT101XQ01 | DWTP_LABORATORY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT102XQ01 | DWTP_ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT103XQ01 | DWTP_EER TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT104XQ01 | DWTP_OFFICE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT105XQ01 | DWTP_UPS ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT106XQ01 | DWTP_CHARGER ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT107XQ01 | DWTP_BATTERY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT108XQ01 | DWTP_DEMINERALIZED WATER TREATMENT AREA TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT109XQ01 | DWTP_DWTP-SPARE 1 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60BT110XQ01 | DWTP_DWTP-SPARE 2 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EC101XB01 | DWTP_CH-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EC101XB49 | DWTP_CH-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EC101XB50 | DWTP_CH-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EC102XB01 | DWTP_CH-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EC102XB49 | DWTP_CH-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EC102XB50 | DWTP_CH-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ101XB01 | DWTP_CT-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ101XB49 | DWTP_CT-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ101XB50 | DWTP_CT-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ102XB01 | DWTP_CT-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ102XB49 | DWTP_CT-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ102XB50 | DWTP_CT-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ201XB01 | DWTP_AHU-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ201XB49 | DWTP_AHU-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ201XB50 | DWTP_AHU-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ202XB01 | DWTP_AHU-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ202XB49 | DWTP_AHU-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ202XB50 | DWTP_AHU-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ203XB01 | DWTP_AHU-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ203XB49 | DWTP_AHU-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ203XB50 | DWTP_AHU-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ204XB01 | DWTP_AHU-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ204XB49 | DWTP_AHU-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ204XB50 | DWTP_AHU-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ205XB01 | DWTP_AHU-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ205XB49 | DWTP_AHU-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ205XB50 | DWTP_AHU-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ206XB01 | DWTP_AHU-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ206XB49 | DWTP_AHU-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ206XB50 | DWTP_AHU-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ207XB01 | DWTP_AHU-207 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ207XB49 | DWTP_AHU-207 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ207XB50 | DWTP_AHU-207 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ208XB01 | DWTP_AHU-208 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ208XB49 | DWTP_AHU-208 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ208XB50 | DWTP_AHU-208 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ209XB01 | DWTP_AHU-209 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ209XB49 | DWTP_AHU-209 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ209XB50 | DWTP_AHU-209 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ210XB01 | DWTP_AHU-210 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ210XB49 | DWTP_AHU-210 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ210XB50 | DWTP_AHU-210 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ211XB01 | DWTP_AHU-211 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ211XB49 | DWTP_AHU-211 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ211XB50 | DWTP_AHU-211 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ212XB01 | DWTP_AHU-212 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ212XB49 | DWTP_AHU-212 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ212XB50 | DWTP_AHU-212 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ213XB01 | DWTP_AHU-213 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ213XB49 | DWTP_AHU-213 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ213XB50 | DWTP_AHU-213 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ214XB01 | DWTP_AHU-214 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ214XB49 | DWTP_AHU-214 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ214XB50 | DWTP_AHU-214 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ501XB01 | DWTP_ACU-501 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ501XB49 | DWTP_ACU-501 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ501XB50 | DWTP_ACU-501 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ502XB01 | DWTP_ACU-502 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ502XB49 | DWTP_ACU-502 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60EQ502XB50 | DWTP_ACU-502 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP101XB01 | DWTP_CHP-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP101XB49 | DWTP_CHP-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP101XB50 | DWTP_CHP-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP102XB01 | DWTP_CHP-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP102XB49 | DWTP_CHP-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP102XB50 | DWTP_CHP-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP201XB01 | DWTP_CWP-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP201XB49 | DWTP_CWP-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP201XB50 | DWTP_CWP-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP202XB01 | DWTP_CWP-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP202XB49 | DWTP_CWP-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60GP202XB50 | DWTP_CWP-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP101XB01 | DWTP_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP101XB49 | DWTP_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP101XB50 | DWTP_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP102XB01 | DWTP_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP102XB49 | DWTP_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP102XB50 | DWTP_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP103XB01 | DWTP_SPARE-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP103XB49 | DWTP_SPARE-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP103XB50 | DWTP_SPARE-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP104XB01 | DWTP_SPARE-104 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP104XB49 | DWTP_SPARE-104 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP104XB50 | DWTP_SPARE-104 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP105XB01 | DWTP_SPARE-105 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP105XB49 | DWTP_SPARE-105 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA60SP105XB50 | DWTP_SPARE-105 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BM101XQ01 | WWTP_ELECTRONIC EQUIPMENT ROOM HUMIDITY | D-AI | 4-20mA | S | 90 | - | - | 20 | % | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BM102XQ01 | WWTP_ELECTRICAL ROOM -1 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BM103XQ01 | WWTP_ELECTRICAL ROOM -2 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BM104XQ01 | WWTP_MCC ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BM106XQ01 | WWTP_WWTP-SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BT101XQ01 | WWTP_ELECTRONIC EQUIPMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BT102XQ01 | WWTP_ELECTRICAL ROOM -1 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BT103XQ01 | WWTP_ELECTRICAL ROOM -2 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BT104XQ01 | WWTP_MCC ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BT105XQ01 | WWTP_1F TANK AREA TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BT106XQ01 | WWTP_2F TANK AREA TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61BT107XQ01 | WWTP_WWTP-SPARE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EC101XB01 | WWTP_CH-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EC101XB49 | WWTP_CH-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EC101XB50 | WWTP_CH-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EC102XB01 | WWTP_CH-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EC102XB49 | WWTP_CH-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EC102XB50 | WWTP_CH-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ101XB01 | WWTP_CT-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ101XB49 | WWTP_CT-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ101XB50 | WWTP_CT-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ102XB01 | WWTP_CT-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ102XB49 | WWTP_CT-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ102XB50 | WWTP_CT-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ201XB01 | WWTP_AHU-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ201XB49 | WWTP_AHU-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ201XB50 | WWTP_AHU-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ202XB01 | WWTP_AHU-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ202XB49 | WWTP_AHU-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ202XB50 | WWTP_AHU-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ203XB01 | WWTP_AHU-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ203XB49 | WWTP_AHU-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ203XB50 | WWTP_AHU-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ204XB01 | WWTP_AHU-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ204XB49 | WWTP_AHU-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ204XB50 | WWTP_AHU-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ205XB01 | WWTP_AHU-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ205XB49 | WWTP_AHU-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ205XB50 | WWTP_AHU-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ206XB01 | WWTP_AHU-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ206XB49 | WWTP_AHU-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ206XB50 | WWTP_AHU-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ207XB01 | WWTP_AHU-207 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ207XB49 | WWTP_AHU-207 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ207XB50 | WWTP_AHU-207 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ208XB01 | WWTP_AHU-208 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ208XB49 | WWTP_AHU-208 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ208XB50 | WWTP_AHU-208 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ501XB01 | WWTP_ACU-501 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ501XB49 | WWTP_ACU-501 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61EQ501XB50 | WWTP_ACU-501 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP101XB01 | WWTP_CHP-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP101XB49 | WWTP_CHP-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP101XB50 | WWTP_CHP-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP102XB01 | WWTP_CHP-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP102XB49 | WWTP_CHP-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP102XB50 | WWTP_CHP-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP201XB01 | WWTP_CWP-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP201XB49 | WWTP_CWP-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP201XB50 | WWTP_CWP-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP202XB01 | WWTP_CWP-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP202XB49 | WWTP_CWP-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61GP202XB50 | WWTP_CWP-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP101XB01 | WWTP_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP101XB49 | WWTP_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP101XB50 | WWTP_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP102XB01 | WWTP_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP102XB49 | WWTP_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP102XB50 | WWTP_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP103XB01 | WWTP_SPARE-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP103XB49 | WWTP_SPARE-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP103XB50 | WWTP_SPARE-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP104XB01 | WWTP_SPARE-104 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP104XB49 | WWTP_SPARE-104 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA61SP104XB50 | WWTP_SPARE-104 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62BM101XQ01 | RWTP_ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62BM102XQ01 | RWTP_RWTP-SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62BT101XQ01 | RWTP_ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62BT102XQ01 | RWTP_RWTP-SPARE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62EC201XB01 | RWTP_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62EC201XB49 | RWTP_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62EC201XB50 | RWTP_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62EC202XB01 | RWTP_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62EC202XB49 | RWTP_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62EC202XB50 | RWTP_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62SP101XB01 | RWTP_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62SP101XB49 | RWTP_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA62SP101XB50 | RWTP_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | DWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BJ101XQ01 | SEH_HVAC CH-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ102XQ01 | SEH_HVAC CH-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ103XQ01 | SEH_HVAC CHP-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ104XQ01 | SEH_HVAC CHP-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ105XQ01 | SEH_HVAC CWP-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ106XQ01 | SEH_HVAC CWP-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ107XQ01 | SEH_HVAC AHU-209 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ108XQ01 | SEH_HVAC AHU-210 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ109XQ01 | SEH_HVAC AHU-211 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ110XQ01 | SEH_HVAC AHU-212 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ111XQ01 | SEH_HVAC AHU-213 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ112XQ01 | SEH_HVAC AHU-214 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ113XQ01 | SEH_HVAC AHU-215 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ114XQ01 | SEH_HVAC FAN-307 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ115XQ01 | SEH_HVAC FAN-308 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ116XQ01 | SEH_HVAC FAN-309 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ117XQ01 | SEH_HVAC FAN-310 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ118XQ01 | SEH_HVAC CT-101 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ119XQ01 | SEH_HVAC CT-102 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BJ120XQ01 | SEH_HVAC ACU-502 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA63BM101XQ01 | SEH_CWP ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BM102XQ01 | SEH_LABORATORY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BM103XQ01 | SEH_ELECTRONIC EQUIPMENT ROOM HUMIDITY | D-AI | 4-20mA | S | 90 | - | - | 20 | % | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BM104XQ01 | SEH_ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BM105XQ01 | SEH_BATTERY ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BM106XQ01 | SEH_CHARGER ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BM107XQ01 | SEH_UPS ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BM108XQ01 | SEH_TRANSFOR/RECTIFIER ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BM109XQ01 | SEH_SEH-SPARE 1 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BM110XQ01 | SEH_SEH-SPARE 2 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT101XQ01 | SEH_CWP ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT102XQ01 | SEH_LABORATORY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT103XQ01 | SEH_ELECTRONIC EQUIPMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT104XQ01 | SEH_ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT105XQ01 | SEH_BATTERY ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT106XQ01 | SEH_CHARGER ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT107XQ01 | SEH_UPS ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT108XQ01 | SEH_TRANSFOR/RECTIFIER ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT109XQ01 | SEH_SEAWATER ELECTROLYSIS ROOM TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT110XQ01 | SEH_SEH-SPARE 1 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63BT111XQ01 | SEH_SEH-SPARE 2 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EC101XB01 | SEH_CH-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EC101XB49 | SEH_CH-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EC101XB50 | SEH_CH-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EC102XB01 | SEH_CH-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EC102XB49 | SEH_CH-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EC102XB50 | SEH_CH-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ101XB01 | SEH_CT-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ101XB49 | SEH_CT-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ101XB50 | SEH_CT-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ102XB01 | SEH_CT-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ102XB49 | SEH_CT-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ102XB50 | SEH_CT-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ201XB01 | SEH_AHU-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ201XB49 | SEH_AHU-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ201XB50 | SEH_AHU-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ202XB01 | SEH_AHU-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ202XB49 | SEH_AHU-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ202XB50 | SEH_AHU-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ203XB01 | SEH_AHU-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ203XB49 | SEH_AHU-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ203XB50 | SEH_AHU-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ204XB01 | SEH_AHU-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ204XB49 | SEH_AHU-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ204XB50 | SEH_AHU-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ205XB01 | SEH_AHU-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ205XB49 | SEH_AHU-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ205XB50 | SEH_AHU-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ206XB01 | SEH_AHU-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ206XB49 | SEH_AHU-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ206XB50 | SEH_AHU-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ207XB01 | SEH_AHU-207 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ207XB49 | SEH_AHU-207 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ207XB50 | SEH_AHU-207 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ208XB01 | SEH_AHU-208 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ208XB49 | SEH_AHU-208 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ208XB50 | SEH_AHU-208 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ209XB01 | SEH_AHU-209 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ209XB49 | SEH_AHU-209 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ209XB50 | SEH_AHU-209 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ210XB01 | SEH_AHU-210 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ210XB49 | SEH_AHU-210 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ210XB50 | SEH_AHU-210 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ211XB01 | SEH_AHU-211 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ211XB49 | SEH_AHU-211 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ211XB50 | SEH_AHU-211 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ212XB01 | SEH_AHU-212 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ212XB49 | SEH_AHU-212 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ212XB50 | SEH_AHU-212 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ213XB01 | SEH_AHU-213 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ213XB49 | SEH_AHU-213 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ213XB50 | SEH_AHU-213 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ214XB01 | SEH_AHU-214 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ214XB49 | SEH_AHU-214 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ214XB50 | SEH_AHU-214 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ215XB01 | SEH_AHU-215 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ215XB49 | SEH_AHU-215 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ215XB50 | SEH_AHU-215 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ216XB01 | SEH_AHU-216 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ216XB49 | SEH_AHU-216 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ216XB50 | SEH_AHU-216 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ217XB01 | SEH_AHU-217 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ217XB49 | SEH_AHU-217 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ217XB50 | SEH_AHU-217 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ218XB01 | SEH_AHU-218 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ218XB49 | SEH_AHU-218 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ218XB50 | SEH_AHU-218 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ219XB01 | SEH_AHU-219 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ219XB49 | SEH_AHU-219 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ219XB50 | SEH_AHU-219 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ501XB01 | SEH_ACU-501 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ501XB49 | SEH_ACU-501 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ501XB50 | SEH_ACU-501 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ502XB01 | SEH_ACU-502 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ502XB49 | SEH_ACU-502 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63EQ502XB50 | SEH_ACU-502 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP101XB01 | SEH_CHP-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP101XB49 | SEH_CHP-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP101XB50 | SEH_CHP-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP102XB01 | SEH_CHP-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP102XB49 | SEH_CHP-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP102XB50 | SEH_CHP-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP201XB01 | SEH_CWP-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP201XB49 | SEH_CWP-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP201XB50 | SEH_CWP-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP202XB01 | SEH_CWP-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP202XB49 | SEH_CWP-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63GP202XB50 | SEH_CWP-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP101XB01 | SEH_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP101XB49 | SEH_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP101XB50 | SEH_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP102XB01 | SEH_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP102XB49 | SEH_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP102XB50 | SEH_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP103XB01 | SEH_SPARE-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP103XB49 | SEH_SPARE-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP103XB50 | SEH_SPARE-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP104XB01 | SEH_SPARE-104 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP104XB49 | SEH_SPARE-104 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP104XB50 | SEH_SPARE-104 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP105XB01 | SEH_SPARE-105 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP105XB49 | SEH_SPARE-105 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP105XB50 | SEH_SPARE-105 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP106XB01 | SEH_SPARE-106 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP106XB49 | SEH_SPARE-106 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA63SP106XB50 | SEH_SPARE-106 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | SWE | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64BM101XQ01 | SW_ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64BM102XQ01 | SW_SW-SPARE ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64BT101XQ01 | SW_ELECTRICAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64BT102XQ01 | SW_SW-SPARE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64EC201XB01 | SW_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64EC201XB49 | SW_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64EC201XB50 | SW_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64EC202XB01 | SW_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64EC202XB49 | SW_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64EC202XB50 | SW_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64SP101XB01 | SW_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64SP101XB49 | SW_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA64SP101XB50 | SW_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | WWT | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BM101XQ01 | HPW_HPW-1 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BM102XQ01 | HPW_HPW-2 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BM103XQ01 | HPW_HPW-3 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BM104XQ01 | HPW_HPW-4 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BM105XQ01 | HPW_HPW-5 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BM106XQ01 | HPW_HPW-6 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BM107XQ01 | HPW_HPW-7 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BM108XQ01 | HPW_HPW-8 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BT101XQ01 | HPW_HPW-1 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BT102XQ01 | HPW_HPW-2 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BT103XQ01 | HPW_HPW-3 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BT104XQ01 | HPW_HPW-4 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BT105XQ01 | HPW_HPW-5 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BT106XQ01 | HPW_HPW-6 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BT107XQ01 | HPW_HPW-7 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69BT108XQ01 | HPW_HPW-8 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC201XB01 | HPW_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC201XB49 | HPW_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC201XB50 | HPW_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC202XB01 | HPW_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC202XB49 | HPW_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC202XB50 | HPW_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC203XB01 | HPW_IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC203XB49 | HPW_IAC-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC203XB50 | HPW_IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC204XB01 | HPW_IAC-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC204XB49 | HPW_IAC-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC204XB50 | HPW_IAC-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC205XB01 | HPW_IAC-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC205XB49 | HPW_IAC-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC205XB50 | HPW_IAC-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC206XB01 | HPW_IAC-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC206XB49 | HPW_IAC-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC206XB50 | HPW_IAC-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC207XB01 | HPW_IAC-207 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC207XB49 | HPW_IAC-207 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC207XB50 | HPW_IAC-207 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC208XB01 | HPW_IAC-208 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC208XB49 | HPW_IAC-208 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC208XB50 | HPW_IAC-208 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC209XB01 | HPW_IAC-209 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC209XB49 | HPW_IAC-209 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC209XB50 | HPW_IAC-209 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC210XB01 | HPW_IAC-210 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC210XB49 | HPW_IAC-210 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC210XB50 | HPW_IAC-210 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC211XB01 | HPW_IAC-211 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC211XB49 | HPW_IAC-211 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC211XB50 | HPW_IAC-211 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC212XB01 | HPW_IAC-212 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC212XB49 | HPW_IAC-212 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69EC212XB50 | HPW_IAC-212 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69SP101XB01 | HPW_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69SP101XB49 | HPW_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69SP101XB50 | HPW_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69SP102XB01 | HPW_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69SP102XB49 | HPW_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69SP102XB50 | HPW_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69SP103XB01 | HPW_SPARE-103 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69SP103XB49 | HPW_SPARE-103 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA69SP103XB50 | HPW_SPARE-103 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70BM101XQ01 | FPW/RW_HOUSE ELECTRICAL EQUIPMENT ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70BM102XQ01 | FPW/RW_FPW/RW-SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70BT101XQ01 | FPW/RW_HOUSE ELECTRICAL EQUIPMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70BT102XQ01 | FPW/RW_FPW/RW-SPARE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70EC201XB01 | FPW/RW_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70EC201XB49 | FPW/RW_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70EC201XB50 | FPW/RW_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70EC202XB01 | FPW/RW_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70EC202XB49 | FPW/RW_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70EC202XB50 | FPW/RW_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70EC203XB01 | FPW/RW_IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70EC203XB49 | FPW/RW_IAC-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70EC203XB50 | FPW/RW_IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70SP101XB01 | FPW/RE_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70SP101XB49 | FPW/RE_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA70SP101XB50 | FPW/RE_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | RFW | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71BJ101XQ01 | EDG_HVAC FAN-301 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BJ102XQ01 | EDG_HVAC FAN-302 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BJ103XQ01 | EDG_HVAC FAN-303 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BJ104XQ01 | EDG_HVAC FAN-304 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BJ105XQ01 | EDG_HVAC FAN-305 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BJ106XQ01 | EDG_HVAC IAC-201 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BJ107XQ01 | EDG_HVAC IAC-202 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BJ108XQ01 | EDG_HVAC IAC-203 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BJ109XQ01 | EDG_HVAC IAC-204 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BJ110XQ01 | EDG_HVAC IAC-205 CURRENT READING | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | MCC | DCDAS | - | - | -
=Q00XAA71BM101XQ01 | EDG_ELECTRICAL ROOM HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71BM102XQ01 | EDG_ELECTRONIC EQUIPMENT ROOM HUMIDITY | D-AI | 4-20mA | S | 90 | - | - | 20 | % | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71BM103XQ01 | EDG_EDG-SPARE HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71BT101XQ01 | EDG_ELECTIRCAL ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71BT102XQ01 | EDG_ELECTRONIC EQUIPMENT ROOM TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71BT103XQ01 | EDG_EMERGENCY DIESEL GENERATOR ROOM TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71BT104XQ01 | EDG_EDG-SPARE TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC201XB01 | EDG_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC201XB49 | EDG_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC201XB50 | EDG_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC202XB01 | EDG_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC202XB49 | EDG_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC202XB50 | EDG_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC203XB01 | EDG_IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC203XB49 | EDG_IAC-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC203XB50 | EDG_IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC204XB01 | EDG_IAC-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC204XB49 | EDG_IAC-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC204XB50 | EDG_IAC-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC205XB01 | EDG_IAC-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC205XB49 | EDG_IAC-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71EC205XB50 | EDG_IAC-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71SP101XB01 | EDG_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71SP101XB49 | EDG_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA71SP101XB50 | EDG_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | EDG | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72BM101XQ01 | CTEER_CABLE TUNNEL ELECTRICAL ROOM -2 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72BM102XQ01 | CTEER_CABLE TUNNEL ELECTRICAL ROOM -2 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72BM103XQ01 | CTEER_CTEER-SPARE 1 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72BM104XQ01 | CTEER_CTEER-SPARE 2 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 100 | % | 0 | 100 | % | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72BT101XQ01 | CTEER_CABLE TUNNEL ELECTIRCAL ROOM -2 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72BT102XQ01 | CTEER_CABLE TUNNEL ELECTRICAL ROOM -2 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72BT103XQ01 | CTEER_CTEER-SPARE 1 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72BT104XQ01 | CTEER_CTEER-SPARE 2 TEMPERATURE | D-AI | 4-20mA | S | 40 | - | - | 10 | °C | NO | YES | 0 | 50 | °C | 0 | 50 | °C | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC201XB01 | CTEER_IAC-201 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC201XB49 | CTEER_IAC-201 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC201XB50 | CTEER_IAC-201 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC202XB01 | CTEER_IAC-202 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC202XB49 | CTEER_IAC-202 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC202XB50 | CTEER_IAC-202 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC203XB01 | CTEER_IAC-203 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC203XB49 | CTEER_IAC-203 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC203XB50 | CTEER_IAC-203 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC204XB01 | CTEER_IAC-204 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC204XB49 | CTEER_IAC-204 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC204XB50 | CTEER_IAC-204 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC205XB01 | CTEER_IAC-205 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC205XB49 | CTEER_IAC-205 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC205XB50 | CTEER_IAC-205 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC206XB01 | CTEER_IAC-206 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC206XB49 | CTEER_IAC-206 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72EC206XB50 | CTEER_IAC-206 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72SP101XB01 | CTEER_SPARE-101 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72SP101XB49 | CTEER_SPARE-101 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72SP101XB50 | CTEER_SPARE-101 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72SP102XB01 | CTEER_SPARE-102 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72SP102XB49 | CTEER_SPARE-102 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=Q00XAA72SP102XB50 | CTEER_SPARE-102 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | TUNL1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BM109XQ01 | GTEB1_GTEB1-SPARE 2 HUMIDITY | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 100 | % | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55BT109XQ01 | GTEB1_GTEB1-SPARE 2 TEMPERATURE | D-AI | 4-20mA | S | - | 40 | 10 | - | °C | NO | YES | - | - | - | 0 | 50 | °C | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ601XB01 | GTEB1_DX-AHU-601 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ601XB49 | GTEB1_DX-AHU-601 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ601XB50 | GTEB1_DX-AHU-601 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ602XB01 | GTEB1_DX-AHU-602 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ602XB49 | GTEB1_DX-AHU-602 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C10XAA55EQ602XB50 | GTEB1_DX-AHU-602 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT1 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BM109XQ01 | GTEB2_GTEB1-SPARE 2 TEMPERATURE | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 100 | % | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55BT109XQ01 | GTEB2_GTEB1-SPARE 2 HUMIDITY | D-AI | 4-20mA | S | - | 40 | 10 | - | °C | NO | YES | - | - | - | 0 | 50 | °C | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ601XB01 | GTEB2_DX-AHU-601 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ601XB49 | GTEB2_DX-AHU-601 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ601XB50 | GTEB2_DX-AHU-601 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ602XB01 | GTEB2_DX-AHU-602 RUNNING STATUS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ602XB49 | GTEB2_DX-AHU-602 ELECTRICAL TRIP | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C20XAA55EQ602XB50 | GTEB2_DX-AHU-602 POWER NORMAL STATUS | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | HVAC | GT2 | ITB part6 sec13 | - | HVAC PLC | DCDAS | - | - | -
=C00QEA01BP001XG52 | PA RECEIVER FOR PWR BLK OUTL PSL | D-DI | 24VDC | S | - | - | 0.65 | - | MPaG | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Pressure Switch | FIELD | DCDAS | - | - | -
=C00QEA01BP302XQ01 | PA RECEIVER FOR PWR BLK OUTL PIT | D-AI | 4-20mA | S | - | - | 0.65 | - | MPaG | NO | YES | - | - | - | 0 | 1.7 | MPaG | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00QEA01QM061XB62 | TO AIR DRYER FOR PWR BLK XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00QEA01QM061XG01 | TO AIR DRYER FOR PWR BLK XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00QEA01QM061XG02 | TO AIR DRYER FOR PWR BLK XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00QEA21BS611XQ01 | COMPRESSOR # A MOTOR DE VIBRATION X | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA21BS611XQ01 | COMPRESSOR # A MOTOR DE VIBRATION Y | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA21BS613XQ01 | COMPRESSOR # A MOTOR NDE VIBRATION X | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA21BS614XQ01 | COMPRESSOR # A MOTOR NDE VIBRATION Y | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA22BS611XQ01 | COMPRESSOR # B MOTOR DE VIBRATION X | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA22BS611XQ01 | COMPRESSOR # B MOTOR DE VIBRATION Y | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA22BS613XQ01 | COMPRESSOR # B MOTOR NDE VIBRATION X | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA22BS614XQ01 | COMPRESSOR # B MOTOR NDE VIBRATION Y | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA23BS611XQ01 | COMPRESSOR # C MOTOR DE VIBRATION X | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA23BS611XQ01 | COMPRESSOR # C MOTOR DE VIBRATION Y | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA23BS613XQ01 | COMPRESSOR # C MOTOR NDE VIBRATION X | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QEA23BS614XQ01 | COMPRESSOR # C MOTOR NDE VIBRATION Y | V-AI | 4-20mA | S | 28 | 11.2 | - | - | mm/s | NO | YES | 0 | 5 | V | 0 | 1270 | μm | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6001 | Virbration Sensor | FIELD | VAMS | - | - | -
=C00QFA01BP001XG52 | AFTERFILTER FOR PWR BLK OULT PSL | D-DI | 24VDC | S | - | - | 0.62 | - | MPaG | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Pressure Switch | FIELD | DCDAS | - | - | -
=C00QFA01BP302XQ01 | AFTERFILTER FOR PWR BLK OULT A PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 1.44 | MPaG | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00QFA01BP303XQ01 | AFTERFILTER FOR PWR BLK OULT B PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 1.44 | MPaG | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00QFA01BP304XQ01 | AFTERFILTER FOR PWR BLK OULT C PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 1.44 | MPaG | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00QFA01BT301XQ01 | AFTERFILTER FOR PWR BLK OULT TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 100 | ℃ | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00QFA01QN001XG01 | FR AFTERFILTER TO IA HDR FOR PWR BLK 01 CV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00QFA01QN001XG02 | FR AFTERFILTER TO IA HDR FOR PWR BLK 01 CV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00QFA01QN001XQ01 | FR AFTERFILTER TO IA HDR FOR PWR BLK 01 CV-ZT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00QFA01QN001XQ23 | FR AFTERFILTER TO IA HDR FOR PWR BLK 01 CV-PY | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C00QFA01QN002XG01 | FR AFTERFILTER TO IA HDR FOR PWR BLK 02 CV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00QFA01QN002XG02 | FR AFTERFILTER TO IA HDR FOR PWR BLK 02 CV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00QFA01QN002XQ01 | FR AFTERFILTER TO IA HDR FOR PWR BLK 02 CV-ZT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00QFA01QN002XQ23 | FR AFTERFILTER TO IA HDR FOR PWR BLK 02 CV-PY | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | ST1 | TC0-1-UEM02-D6002 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C00QEA01BP051XG52 | PA RECEIVER FOR SWES & CWP OUTL PSL | D-DI | 24VDC | S | - | - | 0.62 | - | MPaG | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | Pressure Switch | FIELD | DCDAS | - | - | -
=C00QEA01BP352XQ01 | PA RECEIVER FOR SWES & CWP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.62 | - | MPaG | NO | YES | - | - | - | 0 | 1.38 | MPaG | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00QEA01QM161XB62 | TO AIR DRYER FOR SWES & CWP XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00QEA01QM161XG01 | TO AIR DRYER FOR SWES & CWP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00QEA01QM161XG02 | TO AIR DRYER FOR SWES & CWP XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00QEA24GQ001BS01 | AIR COMP A FOR SWES & CWP VIB | V-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | - | LCP | VAMS | - | - | -
=C00QEA24GQ001BS02 | AIR COMP A FOR SWES & CWP VIB | V-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | - | LCP | VAMS | - | - | -
=C00QEA24GQ001BS03 | AIR COMP A FOR SWES & CWP VIB | V-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | - | LCP | VAMS | - | - | -
=C00QEA24GQ001BS04 | AIR COMP A FOR SWES & CWP VIB | V-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | - | LCP | VAMS | - | - | -
=C00QEA25GQ001BS01 | AIR COMP B FOR SWES & CWP VIB | V-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | - | LCP | VAMS | - | - | -
=C00QEA25GQ001BS02 | AIR COMP B FOR SWES & CWP VIB | V-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | - | LCP | VAMS | - | - | -
=C00QEA25GQ001BS03 | AIR COMP B FOR SWES & CWP VIB | V-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | - | LCP | VAMS | - | - | -
=C00QEA25GQ001BS04 | AIR COMP B FOR SWES & CWP VIB | V-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6003 | - | LCP | VAMS | - | - | -
=C00QFA01BP051XG52 | AFTERFILTER FOR SWES & CWP OULT PSL | D-DI | 24VDC | S | - | - | 0.55 | - | MPaG | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6004 | Pressure Switch | FIELD | DCDAS | - | - | -
=C00QFA01BP352XQ01 | AFTERFILTER FOR SWES & CWP OULT PIT | D-AI | 4-20mA | S | - | - | 0.55 | - | MPaG | NO | YES | - | - | - | 0 | 1.2 | MPaG | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6004 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00QFA01BT351XQ01 | AFTERFILTER FOR SWES & CWP OULT TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 100 | ℃ | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6004 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00QFA01QN101XG01 | FR AFTERFILTER TO IA HDR FOR SWES & CWP CV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6004 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00QFA01QN101XG02 | FR AFTERFILTER TO IA HDR FOR SWES & CWP CV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6004 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00QFA01QN101XQ01 | FR AFTERFILTER TO IA HDR FOR SWES & CWP CV-ZT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6004 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00QFA01QN101XQ23 | FR AFTERFILTER TO IA HDR FOR SWES & CWP CV-PY | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | SWE | TC0-1-UEM02-D6004 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C00QFA01BP311XQ01 | IA RECEIVER FOR NGS PIT | D-AI | 4-20mA | S | - | 0.72 | 0.55 | - | MPaG | NO | YES | - | - | - | 0 | 1.24 | MPaG | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | NGS | TC0-1-UEM02-D6007 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00QFA01BP312XQ01 | TO IA RECEIVER FOR NGS PIT | D-AI | 4-20mA | S | - | 0.72 | 0.55 | - | MPaG | NO | YES | - | - | - | 0 | 1.24 | MPaG | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | NGS | TC0-1-UEM02-D6007 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00QFA01QM061XB62 | TO IA RECV FOR NGS XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | NGS | TC0-1-UEM02-D6007 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00QFA01QM061XG01 | TO IA RECV FOR NGS XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | NGS | TC0-1-UEM02-D6007 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00QFA01QM061XG02 | TO IA RECV FOR NGS XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | INSTRUMENT AIR AND PLANT AIR SYSTEM (COMMON) | NGS | TC0-1-UEM02-D6007 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GAY00XD501XB35 | RAW WTR EER PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | RFW | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GAY00XD501XB36 | RAW WTR EER PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | RFW | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GAY00XD501XB40 | RAW WTR EER PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | RFW | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GAY00XD501XQ01 | RAW WTR HSE PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | RFW | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GAY00XD501XQ02 | RAW WTR EER PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | RFW | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD501XB35 | SWE PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD501XB36 | SWE PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD501XB40 | SWE PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD501XQ01 | SWE PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD501XQ02 | SWE PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD502XB35 | SWE PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD502XB36 | SWE PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD502XB40 | SWE PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD502XB48 | SWE PDP STS ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD502XQ01 | SWE PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GBY00XD502XQ02 | SWE PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | SWE | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD501XB35 | DWTP PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD501XB36 | DWTP PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD501XB40 | DWTP PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD501XB48 | DWTP PDP STS ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD501XQ01 | DWTP PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD501XQ02 | DWTP PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD502XB35 | DWTP PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD502XB36 | DWTP PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD502XB40 | DWTP PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD502XB48 | DWTP PDP STS ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD502XQ01 | DWTP PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GCY00XD502XQ02 | DWTP PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | DWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD501XB35 | CABLE TUNL EER1 PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | TUNL1 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD501XB36 | CABLE TUNL EER1 PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | TUNL1 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD501XB40 | CABLE TUNL EER1 PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | TUNL1 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD501XQ01 | CABLE TUNL EER1 PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | TUNL1 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD501XQ02 | CABLE TUNL EER1 PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | TUNL1 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD502XB35 | CABLE TUNL EER2 PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | TUNL2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD502XB36 | CABLE TUNL EER2 PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | TUNL2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD502XB40 | CABLE TUNL EER2 PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | TUNL2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD502XQ01 | CABLE TUNL EER2 PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | TUNL2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GMZ00XD502XQ02 | CABLE TUNL EER2 PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | TUNL2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD501XB35 | WWTP PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD501XB36 | WWTP PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD501XB40 | WWTP PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD501XQ01 | WWTP PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD501XQ02 | WWTP PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD502XB35 | WWTP PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD502XB36 | WWTP PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD502XB40 | WWTP PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD502XB48 | WWTP PDP STS ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD502XQ01 | WWTP PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00GNY00XD502XQ02 | WWTP PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | WWT | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00MJY00XD501XB35 | EDG PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | EDG | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00MJY00XD501XB36 | EDG PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | EDG | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00MJY00XD501XB40 | EDG PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | EDG | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00MJY00XD501XB48 | EDG PDP STS ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | EDG | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00MJY00XD501XQ01 | EDG PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | EDG | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00MJY00XD501XQ02 | EDG PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | EDG | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00NEY00XD501XB35 | TIAC PDP AX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | GT2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00NEY00XD501XB36 | TIAC PDP BX UV ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | GT2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00NEY00XD501XB40 | TIAC PDP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | PDP | GT2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00NEY00XD501XQ01 | TIAC PDP AX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | GT2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00NEY00XD501XQ02 | TIAC PDP BX VT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | PDP | GT2 | ITB C0-E-NP-004 | - | PDP | DCDAS | - | - | -
=C00XLA01BF301XB27 | PW TK INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 180 | m3/hr | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF301XQ01 | PW TK INL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 180 | m3/hr | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF302XB27 | FR PW TRANS PP FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 180 | m3/hr | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF302XQ01 | FR PW TRANS PP FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 180 | m3/hr | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BL007XG01 | PW TK LSH | D-DI | 24VDC | S | - | 5220 | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00XLA01BL007XG03 | PW TK LSHH | D-DI | 24VDC | S | 5510 | - | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00XLA01BL007XG52 | PW TK LSL | D-DI | 24VDC | S | - | - | 580 | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00XLA01BL007XG54 | PW TK LSLL | D-DI | 24VDC | S | - | - | - | 300 | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00XLA01BL307XQ01 | PW TK LIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 5633 | mmH2O | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BP001XG52 | PW TRANS PP OUTL PS L | D-DI | 24VDC | S | - | - | 0.599 | - | MPaG | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Pressure Switch | FIELD | DCDAS | - | - | -
=C00XLA01BP301XQ01 | PW TRANS PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BP302XQ01 | PW TRANS PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BP303XQ01 | PW TRANS PP C INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BP304XQ01 | PW TRANS PP OUTL PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 1.26 | MPaG | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00XLA01GP501XB01 | PW TRANS PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP501XB49 | PW TRANS PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP501XB50 | PW TRANS PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP501XB61 | PW TRANS PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | DCDAS | EMCC | - | - | -
=C00XLA01GP501XB62 | PW TRANS PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | DCDAS | EMCC | - | - | -
=C00XLA01GP501XB69 | PW TRANS PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | DCDAS | EMCC | - | - | -
=C00XLA01GP501XB78 | PW TRANS PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP501XQ01 | PW TRANS PP A AMP | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP511XB01 | PW TRANS PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP511XB49 | PW TRANS PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP511XB50 | PW TRANS PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP511XB61 | PW TRANS PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | DCDAS | EMCC | - | - | -
=C00XLA01GP511XB62 | PW TRANS PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | DCDAS | EMCC | - | - | -
=C00XLA01GP511XB69 | PW TRANS PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | DCDAS | EMCC | - | - | -
=C00XLA01GP511XB78 | PW TRANS PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP511XQ01 | PW TRANS PP B AMP | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP521XB01 | PW TRANS PP C ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP521XB49 | PW TRANS PP C ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP521XB50 | PW TRANS PP C PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP521XB61 | PW TRANS PP C ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | DCDAS | EMCC | - | - | -
=C00XLA01GP521XB62 | PW TRANS PP C OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | DCDAS | EMCC | - | - | -
=C00XLA01GP521XB69 | PW TRANS PP C STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | DCDAS | EMCC | - | - | -
=C00XLA01GP521XB78 | PW TRANS PP C REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01GP521XQ01 | PW TRANS PP C AMP | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | - | EMCC | DCDAS | - | - | -
=C00XLA01QM081XB01 | PW TK INL MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XLA01QM081XB02 | PW TK INL MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XLA01QM081XB20 | PW TK INL MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XLA01QM081XB49 | PW TK INL MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | MCC | DCDAS | - | - | -
=C00XLA01QM081XB50 | PW TK INL MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | MCC | DCDAS | - | - | -
=C00XLA01QM081XB61 | PW TK INL MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | DCDAS | MCC | - | - | -
=C00XLA01QM081XB62 | PW TK INL MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | DCDAS | MCC | - | - | -
=C00XLA01QM081XB63 | PW TK INL MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XLA01QM081XB64 | PW TK INL MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XLA01QM081XB87 | PW TK INL MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XLA01QM081XB88 | PW TK INL MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XLA01QM081XG33 | PW TK INL MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XLA01QM081XG34 | PW TK INL MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6201 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XLA01BF303XB27 | PW BUFF TK FOR AWWTS & WWTS BLD INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF303XQ01 | PW BUFF TK FOR AWWTS & WWTS BLD INL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF304XB27 | PW BUFF TK FOR GT ELEC BLD INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF304XQ01 | PW BUFF TK FOR GT ELEC BLD INL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF307XB27 | PW TO EMRG SPY VAPOR SUPPR U1 & U2 GT FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | GT2 | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF307XQ01 | PW TO EMRG SPY VAPOR SUPPR U1 & U2 GT FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | GT2 | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF310XB27 | TO ADMIN BLD FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 2 | m3/hr | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF310XQ01 | TO ADMIN BLD FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 2 | m3/hr | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF315XQ01 | PW TO AWWTS & WWTS HVAC FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 2 | m3/hr | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF316XQ01 | PW TO U1 & U2 GT HVAC FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 30 | m3/hr | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF323XQ01 | PW TO GT MAINT (POT) FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF324XQ01 | PW TO HVY PT WHSE / SPARE WHSE (POT) FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF325XQ01 | PW TO AWWTS & WWTS BLD (POT) FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF326XQ01 | PW TO EDG BLD FF ROOF TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF327XQ01 | PW TO SPARE WHSE FF ROOF TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF328XQ01 | PW TO GT MAINT FF ROOF TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6202 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BL001XG01 | PW BUFF TK FOR AWWTS & WWTS BLD LIS H | D-DI | 24VDC | S | - | 3240 | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL001XG03 | PW BUFF TK FOR AWWTS & WWTS BLD LIS HH | D-DI | 24VDC | S | 3420 | - | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL001XG52 | PW BUFF TK FOR AWWTS & WWTS BLD LIS L | D-DI | 24VDC | S | - | - | 360 | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL001XG54 | PW BUFF TK FOR AWWTS & WWTS BLD LIS LL | D-DI | 24VDC | S | - | - | - | 180 | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL002XG01 | PW BUFF TK FOR GT ELEC BLD LIS H | D-DI | 24VDC | S | - | 3240 | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL002XG03 | PW BUFF TK FOR GT ELEC BLD LIS HH | D-DI | 24VDC | S | 3420 | - | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL002XG52 | PW BUFF TK FOR GT ELEC BLD LIS L | D-DI | 24VDC | S | - | - | 360 | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL002XG54 | PW BUFF TK FOR GT ELEC BLD LIS LL | D-DI | 24VDC | S | - | - | - | 180 | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01QM061XB61 | PW BUFF TK FOR AWWTS & WWTS BLD INL XV-OPN | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XLA01QM061XG01 | PW BUFF TK FOR AWWTS & WWTS BLD INL XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM061XG02 | PW BUFF TK FOR AWWTS & WWTS BLD INL XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | WWT | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM062XB61 | PW BUFF TK FOR GT ELEC BLD INL XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XLA01QM062XG01 | PW BUFF TK FOR GT ELEC BLD INL XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM062XG02 | PW BUFF TK FOR GT ELEC BLD INL XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT1 | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM067XB61 | TO ADMIN BLD XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XLA01QM067XG01 | TO ADMIN BLD XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM067XG02 | TO ADMIN BLD XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM068XB61 | TO TIAC SYS XV OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT2 | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XLA01QM068XG01 | TO TIAC SYS XV VLV OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT2 | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM068XG02 | TO TIAC SYS XV VLV CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | GT2 | TC0-1-URM02-D6202 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01BF305XB27 | PW BUFF TK FOR MCB INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF305XQ01 | PW BUFF TK FOR MCB INL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF306XB27 | PW BUFF TK FOR DWTS BLD INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF306XQ01 | PW BUFF TK FOR DWTS BLD INL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF317XQ01 | PW HDR TO MAIN CTRL BULD BULD HVAC FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 6 | m3/hr | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF318XQ01 | PW HDR TO DWTS BULD HVAC FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 2 | m3/hr | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF329XQ01 | PW TO SAF SHWR (CMN) FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6203 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF330XQ01 | PW TO SAF SHWR IN RWS BLD FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6203 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF331XQ01 | PW TO DEMIN TREAT BLD (POT) FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6203 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BL003XG01 | PW BUFF TK FOR MCB LIS H | D-DI | 24VDC | S | - | 3240 | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL003XG03 | PW BUFF TK FOR MCB LIS HH | D-DI | 24VDC | S | 3420 | - | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL003XG52 | PW BUFF TK FOR MCB LIS L | D-DI | 24VDC | S | - | - | 360 | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL003XG54 | PW BUFF TK FOR MCB LIS LL | D-DI | 24VDC | S | - | - | - | 180 | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL004XG01 | PW BUFF TK FOR DWTS BLD LIS H | D-DI | 24VDC | S | - | 3240 | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL004XG03 | PW BUFF TK FOR DWTS BLD LIS HH | D-DI | 24VDC | S | 3420 | - | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL004XG52 | PW BUFF TK FOR DWTS BLD LIS L | D-DI | 24VDC | S | - | - | 360 | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL004XG54 | PW BUFF TK FOR DWTS BLD LIS LL | D-DI | 24VDC | S | - | - | - | 180 | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01QM063XB61 | PW BUFF TK FOR MCB INL XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XLA01QM063XG01 | PW BUFF TK FOR MCB INL XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM063XG02 | PW BUFF TK FOR MCB INL XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6203 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM064XB61 | PW BUFF TK FOR DWTS BLD INL XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XLA01QM064XG01 | PW BUFF TK FOR DWTS BLD INL XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM064XG02 | PW BUFF TK FOR DWTS BLD INL XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6203 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01BF308XB27 | PW BUFF TK FOR ST ELEC BLD INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF308XQ01 | PW BUFF TK FOR ST ELEC BLD INL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF309XB27 | PW BUFF TK FOR SWES & CWP INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF309XQ01 | PW BUFF TK FOR SWES & CWP INL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 10 | m3/hr | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF314XB27 | TO UPW REGEN SYSTEM FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 6 | m3/hr | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF314XQ01 | TO UPW REGEN SYSTEM FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 6 | m3/hr | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF319XQ01 | PW TO U1 & U2 ST HVAC & ELEC BLD FF ROOF TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 6 | m3/hr | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF320XQ01 | PW TO SWES FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 9 | m3/hr | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF321XQ01 | PW TO SWES & CWP HSE FF & HVAC & UTLY STN FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 6 | m3/hr | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF332XQ01 | PW TO SWE HSE (POT) FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF333XQ01 | PW TO CWP HSE (POT) FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF334XQ01 | PW TO U1 & U2 ST ELEC BLD (POT) FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF335XQ01 | PW TO SAF SHWR IN NG TREAT & NGS (POT) FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | POTABLE WATER SYSTEM (COMMON) | HOLD | TC0-1-URM02-D6204 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BL005XG01 | PW BUFF TK FOR ST ELEC BLD LIS H | D-DI | 24VDC | S | - | 3240 | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL005XG03 | PW BUFF TK FOR ST ELEC BLD LIS HH | D-DI | 24VDC | S | 3420 | - | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL005XG52 | PW BUFF TK FOR ST ELEC BLD LIS L | D-DI | 24VDC | S | - | - | 360 | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL005XG54 | PW BUFF TK FOR ST ELEC BLD LIS LL | D-DI | 24VDC | S | - | - | - | 180 | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL006XG01 | PW BUFF TK FOR SWES & CWP LIS H | D-DI | 24VDC | S | - | 3240 | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL006XG03 | PW BUFF TK FOR SWES & CWP LIS HH | D-DI | 24VDC | S | 3420 | - | - | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL006XG52 | PW BUFF TK FOR SWES & CWP LIS L | D-DI | 24VDC | S | - | - | 360 | - | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01BL006XG54 | PW BUFF TK FOR SWES & CWP LIS LL | D-DI | 24VDC | S | - | - | - | 180 | mm | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C00XLA01QM065XB61 | PW BUFF TK FOR ST ELEC BLD INL XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XLA01QM065XG01 | PW BUFF TK FOR ST ELEC BLD INL XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM065XG02 | PW BUFF TK FOR ST ELEC BLD INL XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | ST1 | TC0-1-URM02-D6204 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM066XB61 | PW BUFF TK FOR SWES & CWP INL XV-OPN | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00XLA01QM066XG01 | PW BUFF TK FOR SWES & CWP INL XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01QM066XG02 | PW BUFF TK FOR SWES & CWP INL XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | POTABLE WATER SYSTEM (COMMON) | SWE | TC0-1-URM02-D6204 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00XLA01BF311XB27 | TO SAFETY SHOWER CMN FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 7 | m3/hr | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6205 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF311XQ01 | TO SAFETY SHOWER CMN FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 7 | m3/hr | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6205 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF312XB27 | TO NH3 ACC SPRINKER FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 26 | m3/hr | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6205 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF312XQ01 | TO NH3 ACC SPRINKER FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 26 | m3/hr | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6205 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF313XB27 | TO NH3 DIL TK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 75 | m3/hr | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6205 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XLA01BF313XQ01 | TO NH3 DIL TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 75 | m3/hr | POTABLE WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6205 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01QM161XB61 | FR MISC WTR FEED PP TO RAINWTR STG TK XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GAF01QM161XG01 | FR MISC WTR FEED PP TO RAINWTR STG TK XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GAF01QM161XG02 | FR MISC WTR FEED PP TO RAINWTR STG TK XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GNZ01QM161XB61 | FR MISC WTR PP XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00GNZ01QM161XG01 | FR MISC WTR PP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GNZ01QM161XG02 | FR MISC WTR PP XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01BF301XQ01 | RAINWTR STG TK OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 8 | m3/hr | RAINWATER RECOVERY SYSTEM (COMMON) | HOLD | TC0-1-CMM02-D6001 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00XVA01BL301XQ01 | RAINWTR STG TK LIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 200 | 2500 | mm | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | Level transmitter | FIELD | DCDAS | - | - | -
=C00XVA01QM061XB61 | FR MISC WTR FEED PUMP TO RAINWTR STG TK XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM061XG01 | FR MISC WTR FEED PUMP TO RAINWTR STG TK XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM061XG02 | FR MISC WTR FEED PUMP TO RAINWTR STG TK XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01XD801AXB41 | RAINWTR STG TK PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | - | LCP | DCDAS | - | - | -
=C00XVA01XD801AXJ51 | RAINWTR STG TK PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | - | LCP | DCDAS | - | - | -
=C00XVA01XD801BXB41 | RAINWTR STG TK PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | - | LCP | DCDAS | - | - | -
=C00XVA01XD801BXJ51 | RAINWTR STG TK PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | - | LCP | DCDAS | - | - | -
=C00XVA01XD801XB40 | RAINWTR STG TK LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | - | LCP | DCDAS | - | - | -
=C00XVA01XD801XG01 | RAINWTR STG TK LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | - | LCP | DCDAS | - | - | -
=C00XVA01XD801XG03 | RAINWTR STG TK LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | - | LCP | DCDAS | - | - | -
=C00XVA01XD801XG52 | RAINWTR STG TK LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | - | LCP | DCDAS | - | - | -
=C00XVA01XD801XG54 | RAINWTR STG TK LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | MCB | TC0-1-CMM02-D6001 | - | LCP | DCDAS | - | - | -
=C00XVA01BL311XQ01 | ST RAINWTR RECV BSN LIT | D-AI | 4-20mA | S | 4750 | 4500 | 300 | - | mm | NO | YES | - | - | - | 200 | 6500 | mm | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | Level transmitter | FIELD | DCDAS | - | - | -
=C00XVA01BL321XQ01 | DWTS RAINWTR RECV BSN LIT | D-AI | 4-20mA | S | 4750 | 4500 | 300 | - | mm | NO | YES | - | - | - | 200 | 6500 | mm | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | Level transmitter | FIELD | DCDAS | - | - | -
=C00XVA01BP311XQ01 | RAINWTR FLTR FACIL FOR ST PDIT | D-AI | 4-20mA | S | - | HOLD | - | - | MPa | NO | YES | 0 | HOLD | MPa | 0 | HOLD | MPa | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00XVA01BP321XQ01 | RAINWTR FLTR FACIL FOR DWTS PDIT | D-AI | 4-20mA | S | - | HOLD | - | - | MPa | NO | YES | 0 | HOLD | MPa | 0 | HOLD | MPa | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00XVA01QM062XB61 | TO ST RAINWTR RECV BSN XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM062XG01 | TO ST RAINWTR RECV BSN XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM062XG02 | TO ST RAINWTR RECV BSN XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM063XB62 | RAINWTR HDR TO DITCH OF ST XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM063XG01 | RAINWTR HDR TO DITCH OF ST XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM063XG02 | RAINWTR HDR TO DITCH OF ST XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM064XB61 | TO DWTS RW RECV BSN XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM064XG01 | TO DWTS RW RECV BSN XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM064XG02 | TO DWTS RW RECV BSN XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM065XB62 | RAINWTR HDR TO DITCH OF DWTS XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM065XG01 | RAINWTR HDR TO DITCH OF DWTS XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM065XG02 | RAINWTR HDR TO DITCH OF DWTS XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01XD802AXB41 | ST RAINWTR RECV BSN PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD802AXJ51 | ST RAINWTR RECV BSN PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD802BXB41 | ST RAINWTR RECV BSN PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD802BXJ51 | ST RAINWTR RECV BSN PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD802XB40 | ST RAINWTR RECV BSN LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD802XB62 | RAINWTR STG TK LH TO STOP PP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | DCDAS | LCP | - | - | -
=C00XVA01XD802XG01 | ST RAINWTR RECV BSN LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD802XG03 | ST RAINWTR RECV BSN LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD802XG52 | ST RAINWTR RECV BSN LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD802XG54 | ST RAINWTR RECV BSN LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | ST2 | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD803AXB41 | DWTS RAINWTR RECV BSN PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD803AXJ51 | DWTS RAINWTR RECV BSN PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD803BXB41 | DWTS RAINWTR RECV BSN PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD803BXJ51 | DWTS RAINWTR RECV BSN PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD803XB40 | DWTS RAINWTR RECV BSN LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD803XB62 | RAINWTR STG TK LH TO STOP PP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | DCDAS | LCP | - | - | -
=C00XVA01XD803XG01 | DWTS RAINWTR RECV BSN LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD803XG03 | DWTS RAINWTR RECV BSN LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD803XG52 | DWTS RAINWTR RECV BSN LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01XD803XG54 | DWTS RAINWTR RECV BSN LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | DWT | TC0-1-CMM02-D6002 | - | LCP | DCDAS | - | - | -
=C00XVA01BL331XQ01 | GT RAINWTR RECV BSN LIT | D-AI | 4-20mA | S | 4750 | 4500 | 300 | - | mm | NO | YES | - | - | - | 200 | 6500 | mm | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | Level transmitter | FIELD | DCDAS | - | - | -
=C00XVA01BL341XQ01 | AWWTS & WWTS RAINWTR RECV BSN LIT | D-AI | 4-20mA | S | 4750 | 4500 | 300 | - | mm | NO | YES | - | - | - | 200 | 6500 | mm | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | Level transmitter | FIELD | DCDAS | - | - | -
=C00XVA01BP331XQ01 | RAINWTR FLTR FACIL FOR GT PDIT | D-AI | 4-20mA | S | - | HOLD | - | - | MPa | NO | YES | 0 | HOLD | MPa | 0 | HOLD | MPa | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00XVA01BP341XQ01 | AWWTS & WWTS RAINWTR FLTR FACIL PDIT | D-AI | 4-20mA | S | - | HOLD | - | - | MPa | NO | YES | 0 | HOLD | MPa | 0 | HOLD | MPa | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00XVA01QM066XB61 | TO GT RAINWTR RECV BSN XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM066XG01 | TO GT RAINWTR RECV BSN XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM066XG02 | TO GT RAINWTR RECV BSN XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM067XB62 | RAINWTR HDR TO DITCH OF GT XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM067XG01 | RAINWTR HDR TO DITCH OF GT XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM067XG02 | RAINWTR HDR TO DITCH OF GT XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM068XB61 | TO AWWTS & WWTS RAINWTR RECV BSN XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM068XG01 | TO AWWTS & WWTS RAINWTR RECV BSN XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM068XG02 | TO AWWTS & WWTS RAINWTR RECV BSN XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM069XB62 | RAINWTR HDR TO DITCH OF AWWTS & WWTS XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM069XG01 | RAINWTR HDR TO DITCH OF AWWTS & WWTS XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM069XG02 | RAINWTR HDR TO DITCH OF AWWTS & WWTS XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01XD804AXB41 | GT RAINWTR RECV BSN PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD804AXJ51 | GT RAINWTR RECV BSN PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD804BXB41 | GT RAINWTR RECV BSN PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD804BXJ51 | GT RAINWTR RECV BSN PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD804XB40 | GT RAINWTR RECV BSN LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD804XB62 | RAINWTR STG TK LH TO STOP PP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | DCDAS | LCP | - | - | -
=C00XVA01XD804XG01 | GT RAINWTR RECV BSN LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD804XG03 | GT RAINWTR RECV BSN LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD804XG52 | GT RAINWTR RECV BSN LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD804XG54 | GT RAINWTR RECV BSN LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | GT2 | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD805AXB41 | AWWTS & WWTS RAINWTR RECV BSN PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD805AXJ51 | AWWTS & WWTS RAINWTR RECV BSN PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD805BXB41 | AWWTS & WWTS RAINWTR RECV BSN PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD805BXJ51 | AWWTS & WWTS RAINWTR RECV BSN PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD805XB40 | AWWTS & WWTS RAINWTR RECV BSN LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD805XB62 | RAINWTR STG TK LH TO STOP PP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | DCDAS | LCP | - | - | -
=C00XVA01XD805XG01 | AWWTS & WWTS RAINWTR RECV BSN LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD805XG03 | AWWTS & WWTS RAINWTR RECV BSN LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD805XG52 | AWWTS & WWTS RAINWTR RECV BSN LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01XD805XG54 | AWWTS & WWTS RAINWTR RECV BSN LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | WWT | TC0-1-CMM02-D6003 | - | LCP | DCDAS | - | - | -
=C00XVA01BL351XQ01 | HRSG RAINWTR RECV BSN LIT | D-AI | 4-20mA | S | 4750 | 4500 | 300 | - | mm | NO | YES | - | - | - | 200 | 6500 | mm | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | Level transmitter | FIELD | DCDAS | - | - | -
=C00XVA01BP351XQ01 | RAINWTR FLTR FACIL FOR HRSG PDIT | D-AI | 4-20mA | S | - | HOLD | - | - | MPa | NO | YES | 0 | HOLD | MPa | 0 | HOLD | MPa | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00XVA01QM070XB61 | TO HRSG RAINWTR RECV BSN XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM070XG01 | TO HRSG RAINWTR RECV BSN XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM070XG02 | TO HRSG RAINWTR RECV BSN XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM071XB62 | RAINWTR HDR TO DITCH OF HRSG XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00XVA01QM071XG01 | RAINWTR HDR TO DITCH OF HRSG XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01QM071XG02 | RAINWTR HDR TO DITCH OF HRSG XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00XVA01XD806AXB41 | HRSG RAINWTR RECV BSN PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | LCP | DCDAS | - | - | -
=C00XVA01XD806AXJ51 | HRSG RAINWTR RECV BSN PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | LCP | DCDAS | - | - | -
=C00XVA01XD806BXB41 | HRSG RAINWTR RECV BSN PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | LCP | DCDAS | - | - | -
=C00XVA01XD806BXJ51 | HRSG RAINWTR RECV BSN PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | LCP | DCDAS | - | - | -
=C00XVA01XD806XB40 | HRSG RAINWTR RECV BSN LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | LCP | DCDAS | - | - | -
=C00XVA01XD806XB62 | RAINWTR STG TK LH TO STOP PP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | DCDAS | LCP | - | - | -
=C00XVA01XD806XG01 | HRSG RAINWTR RECV BSN LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | LCP | DCDAS | - | - | -
=C00XVA01XD806XG03 | HRSG RAINWTR RECV BSN LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | LCP | DCDAS | - | - | -
=C00XVA01XD806XG52 | HRSG RAINWTR RECV BSN LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | LCP | DCDAS | - | - | -
=C00XVA01XD806XG54 | HRSG RAINWTR RECV BSN LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAINWATER RECOVERY SYSTEM (COMMON) | HRSG1 | TC0-1-CMM02-D6004 | - | LCP | DCDAS | - | - | -
=C00GHC01BF305XQ01 | DW TRANS PP A & B TO U1 &U2 CNDS STG TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 365 | m3/hr | RAINWATER RECOVERY SYSTEM (COMMON) | HOLD | TC0-1-KDM02-D6101 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF306XQ01 | DW TRANS PP A & B TO EX DW HDR FOR U9 & U10 FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 105 | m3/hr | RAINWATER RECOVERY SYSTEM (COMMON) | HOLD | TC0-1-KDM02-D6101 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF307XQ01 | DW TRANS PP A & B TO DWTS LAB FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 2 | m3/hr | RAINWATER RECOVERY SYSTEM (COMMON) | HOLD | TC0-1-KDM02-D6101 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GHC01BF309XQ01 | DW TRANS PP A & B TO WWTS LAB FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 2 | m3/hr | RAINWATER RECOVERY SYSTEM (COMMON) | HOLD | TC0-1-KDM02-D6101 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF301XB27 | RAW WTR PUMP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | 0 | 2500 | mmH2O | 0 | 500 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF301XQ01 | RAW WTR PUMP OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2500 | mmH2O | 0 | 500 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BL002XG01 | EX #2 RAW WTR & FIRE WTR TK LSH | D-DI | 24VDC | S | - | 4950 | - | - | mm | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GAF01BL002XG52 | EX #2 RAW WTR & FIRE WTR TK LSL | D-DI | 24VDC | S | - | - | 3850 | - | mm | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GAF01BL002XG54 | EX #2 RAW WTR & FIRE WTR TK LSLL | D-DI | 24VDC | S | - | - | - | 2350 | mm | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GAF01BL002XH11 | EX #2 RAW WTR & FIRE WTR TK H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | - | DCDAS | Relay Box | - | - | -
=C00GAF01BL002XH62 | EX #2 RAW WTR & FIRE WTR TK L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | - | DCDAS | Relay Box | - | - | -
=C00GAF01BL302XH11 | EX #2 RAW WTR & FIRE WTR TK H LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Level transmitter | DCDAS | Relay box | - | - | -
=C00GAF01BL302XH62 | EX #2 RAW WTR & FIRE WTR TK L LOC LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Level transmitter | DCDAS | Relay box | - | - | -
=C00GAF01BL302XQ01 | EX #2 RAW WTR & FIRE WTR TK LIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Level transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP001XG52 | RAW WTR PP OUTL PS L | D-DI | 24VDC | S | - | - | 0.701 | - | MPaG | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | Pressure Switch | FIELD | DCDAS | - | - | -
=C00GAF01BP301XQ01 | RAW WTR PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP302XQ01 | RAW WTR PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP303XQ01 | RAW WTR PP OUTL PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 1.476 | MPaG | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01GP501XB01 | RAW WTR PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | MCC | DCDAS | - | - | -
=C00GAF01GP501XB49 | RAW WTR PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | MCC | DCDAS | - | - | -
=C00GAF01GP501XB50 | RAW WTR PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | MCC | DCDAS | - | - | -
=C00GAF01GP501XB61 | RAW WTR PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | DCDAS | MCC | - | - | -
=C00GAF01GP501XB62 | RAW WTR PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | DCDAS | MCC | - | - | -
=C00GAF01GP501XB69 | RAW WTR PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | DCDAS | MCC | - | - | -
=C00GAF01GP501XB78 | RAW WTR PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | MCC | DCDAS | - | - | -
=C00GAF01GP511XB01 | RAW WTR PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | MCC | DCDAS | - | - | -
=C00GAF01GP511XB49 | RAW WTR PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | MCC | DCDAS | - | - | -
=C00GAF01GP511XB50 | RAW WTR PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | MCC | DCDAS | - | - | -
=C00GAF01GP511XB61 | RAW WTR PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | DCDAS | MCC | - | - | -
=C00GAF01GP511XB62 | RAW WTR PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | DCDAS | MCC | - | - | -
=C00GAF01GP511XB69 | RAW WTR PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | DCDAS | MCC | - | - | -
=C00GAF01GP511XB78 | RAW WTR PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6101 | - | MCC | DCDAS | - | - | -
=C00GAF01QM081XB01 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM081XB02 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM081XB20 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM081XB49 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | MCC | DCDAS | - | - | -
=C00GAF01QM081XB50 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | MCC | DCDAS | - | - | -
=C00GAF01QM081XB61 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | DCDAS | MCC | - | - | -
=C00GAF01QM081XB62 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | DCDAS | MCC | - | - | -
=C00GAF01QM081XB63 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00GAF01QM081XB64 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00GAF01QM081XB87 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM081XB88 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM081XG33 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM081XG34 | #1 TO #2 RAW WTR & FIRE WTR TK MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | RFW | TC0-1-URM02-D6101 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01BF302XB27 | RAW WTR BUFF PUMP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 140 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF302XQ01 | RAW WTR BUFF PUMP OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 140 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF306XB27 | FR RAW WTR PP FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | 0 | 2500 | mmH2O | 0 | 500 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF306XQ01 | FR RAW WTR PP FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2500 | mmH2O | 0 | 500 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BL001XG01 | RAW WTR BUFF TK LSH | D-DI | 24VDC | S | - | 13770 | - | - | mm | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GAF01BL001XG03 | RAW WTR BUFF TK LSHH | D-DI | 24VDC | S | 14535 | - | - | - | mm | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GAF01BL001XG52 | RAW WTR BUFF TK LSL | D-DI | 24VDC | S | - | - | 1530 | - | mm | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GAF01BL001XG54 | RAW WTR BUFF TK LSLL | D-DI | 24VDC | S | - | - | - | 765 | mm | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GAF01BL301XQ01 | RAW WTR BUFF TK LIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 15059 | mmH2O | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP304XQ01 | RAW WTR BUFF PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP305XQ01 | RAW WTR BUFF PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP306XQ01 | RAW WTR BUFF PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.61 | - | MPaG | NO | YES | - | - | - | 0 | 1.284 | MPaG | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BT301XQ01 | RAW WTR BUFF TK TIT | D-AI | 4-20mA | S | - | 40 | - | - | ℃ | NO | YES | - | - | - | 0 | 100 | ℃ | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01GP502XB01 | RAW WTR BUFF PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | MCC | DCDAS | - | - | -
=C00GAF01GP502XB49 | RAW WTR BUFF PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | MCC | DCDAS | - | - | -
=C00GAF01GP502XB50 | RAW WTR BUFF PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | MCC | DCDAS | - | - | -
=C00GAF01GP502XB61 | RAW WTR BUFF PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | DCDAS | MCC | - | - | -
=C00GAF01GP502XB62 | RAW WTR BUFF PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | DCDAS | MCC | - | - | -
=C00GAF01GP502XB69 | RAW WTR BUFF PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | DCDAS | MCC | - | - | -
=C00GAF01GP502XB78 | RAW WTR BUFF PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | MCC | DCDAS | - | - | -
=C00GAF01GP512XB01 | RAW WTR BUFF PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | MCC | DCDAS | - | - | -
=C00GAF01GP512XB49 | RAW WTR BUFF PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | MCC | DCDAS | - | - | -
=C00GAF01GP512XB50 | RAW WTR BUFF PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | MCC | DCDAS | - | - | -
=C00GAF01GP512XB61 | RAW WTR BUFF PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | DCDAS | MCC | - | - | -
=C00GAF01GP512XB62 | RAW WTR BUFF PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | DCDAS | MCC | - | - | -
=C00GAF01GP512XB69 | RAW WTR BUFF PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | DCDAS | MCC | - | - | -
=C00GAF01GP512XB78 | RAW WTR BUFF PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | - | MCC | DCDAS | - | - | -
=C00GAF01QM082XB01 | FR RAW WTR PP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM082XB02 | FR RAW WTR PP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM082XB20 | FR RAW WTR PP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM082XB49 | FR RAW WTR PP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | MCC | DCDAS | - | - | -
=C00GAF01QM082XB50 | FR RAW WTR PP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | MCC | DCDAS | - | - | -
=C00GAF01QM082XB61 | FR RAW WTR PP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | DCDAS | MCC | - | - | -
=C00GAF01QM082XB62 | FR RAW WTR PP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | DCDAS | MCC | - | - | -
=C00GAF01QM082XB63 | FR RAW WTR PP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00GAF01QM082XB64 | FR RAW WTR PP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00GAF01QM082XB87 | FR RAW WTR PP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM082XB88 | FR RAW WTR PP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM082XG33 | FR RAW WTR PP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GAF01QM082XG34 | FR RAW WTR PP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Moter Operated Control Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GDA01BF301XB27 | FR AWWTS TO RAW WTR BUFF TANK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 750 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GDA01BF301XQ01 | FR AWWTS TO RAW WTR BUFF TANK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 750 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6102 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF303XB27 | TO UTLY STN FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 6 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF303XQ01 | TO UTLY STN FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 6 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF304XB27 | TO WW SYS FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 22 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF304XQ01 | TO WW SYS FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 22 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF305XB27 | TO PWR ISLAND FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 120 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF305XQ01 | TO PWR ISLAND FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 120 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF308XB27 | TO MISC WTR PP FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 8 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF308XQ01 | TO MISC WTR PP FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 8 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF309XB27 | TO DWT SYS FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 8 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF309XQ01 | TO DWT SYS FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 8 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF310XB27 | TO EDG ROOM FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 6 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF310XQ01 | TO EDG ROOM FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 6 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6103 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF307XB27 | MISC WTR FEED PP OUTL TO MISC WTR TANK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 100 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF307XQ01 | MISC WTR FEED PP OUTL TO MISC WTR TANK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 100 | m3/hr | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BF311XQ01 | MISC WTR FEED PP OUTL TO RAINWTR STOR TANK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 100 | m3/hr | RAW WATER SYSTEM (COMMON) | MCB | TC0-1-URM02-D6104 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP307XQ01 | MISC WTR FEED PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP308XQ01 | MISC WTR FEED PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | D/P Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP309XQ01 | MISC WTR FEED PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.237 | - | MPaG | NO | YES | - | - | - | 0 | 0.498 | MPaG | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01GP503XB01 | MISC WTR FEED PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | MCC | DCDAS | - | - | -
=C00GAF01GP503XB49 | MISC WTR FEED PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | MCC | DCDAS | - | - | -
=C00GAF01GP503XB50 | MISC WTR FEED PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | MCC | DCDAS | - | - | -
=C00GAF01GP503XB61 | MISC WTR FEED PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | DCDAS | MCC | - | - | -
=C00GAF01GP503XB62 | MISC WTR FEED PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | DCDAS | MCC | - | - | -
=C00GAF01GP503XB69 | MISC WTR FEED PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | DCDAS | MCC | - | - | -
=C00GAF01GP503XB78 | MISC WTR FEED PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | MCC | DCDAS | - | - | -
=C00GAF01GP513XB01 | MISC WTR FEED PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | MCC | DCDAS | - | - | -
=C00GAF01GP513XB49 | MISC WTR FEED PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | MCC | DCDAS | - | - | -
=C00GAF01GP513XB50 | MISC WTR FEED PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | MCC | DCDAS | - | - | -
=C00GAF01GP513XB61 | MISC WTR FEED PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | DCDAS | MCC | - | - | -
=C00GAF01GP513XB62 | MISC WTR FEED PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | DCDAS | MCC | - | - | -
=C00GAF01GP513XB69 | MISC WTR FEED PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | DCDAS | MCC | - | - | -
=C00GAF01GP513XB78 | MISC WTR FEED PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RAW WATER SYSTEM (COMMON) | DWT | TC0-1-URM02-D6104 | - | MCC | DCDAS | - | - | -
=C00GTA01BF301XB27 | FR BLDN RECOV TK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | 0 | 2500 | mmH2O | 0 | 142.5 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTA01BF301XQ01 | FR BLDN RECOV TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2500 | mmH2O | 0 | 142.5 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTA01BF302XB27 | FR RECOV WTR SUMP FOR DWTS FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 150 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTA01BF302XQ01 | FR RECOV WTR SUMP FOR DWTS FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 150 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTA01BL001XG01 | BLDN DRAIN SURGE TK A LSH | D-DI | 24VDC | S | - | 7920 | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL001XG03 | BLDN DRAIN SURGE TK A LSHH | D-DI | 24VDC | S | 8360 | - | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL001XG52 | BLDN DRAIN SURGE TK A LSL | D-DI | 24VDC | S | - | - | 880 | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL001XG54 | BLDN DRAIN SURGE TK A LSLL | D-DI | 24VDC | S | - | - | - | 440 | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL002XG01 | BLDN DRAIN SURGE TK B LSH | D-DI | 24VDC | S | - | 7920 | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL002XG03 | BLDN DRAIN SURGE TK B LSHH | D-DI | 24VDC | S | 8360 | - | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL002XG52 | BLDN DRAIN SURGE TK B LSL | D-DI | 24VDC | S | - | - | 880 | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL002XG54 | BLDN DRAIN SURGE TK B LSLL | D-DI | 24VDC | S | - | - | - | 440 | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL301XQ01 | BLDN DRAIN SURGE TK A LIT | D-AI | 4-20mA | S | 8360 | 7920 | 880 | 440 | mm | NO | YES | - | - | - | 200 | 8800 | mm | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Radar Level Transmitter | FIELD | DCDAS | - | - | -
=C00GTA01BL302XQ01 | BLDN DRAIN SURGE TK B LIT | D-AI | 4-20mA | S | 8360 | 7920 | 880 | 440 | mm | NO | YES | - | - | - | 200 | 8800 | mm | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Radar Level Transmitter | FIELD | DCDAS | - | - | -
=C00GTA01BP301XQ01 | BLDN DRAIN FEED PPS A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTA01BP302XQ01 | BLDN DRAIN FEED PPS B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTA01BP303XQ01 | BLDN DRAIN FEED PPS OUTL PIT | D-AI | 4-20mA | S | - | - | 0.26 | - | MPaG | NO | YES | - | - | - | 0 | 0.56 | MPaG | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTA01BQ301XQ01 | BLDN DRAIN SURGE TK A AIT (SS) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 20 | mg/L | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Suspended Solid Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTA01BQ302XQ01 | BLDN DRAIN SURGE TK A AIT (COND) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 532 | μs/cm | 0 | 600 | μs/cm | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Conductivity Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTA01BQ303XQ01 | BLDN DRAIN SURGE TK A AIT (PH) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 14 | pH | 0 | 14 | pH | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | PH Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTA01BQ304XQ01 | BLDN DRAIN SURGE TK B AIT (SS) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 20 | mg/L | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Suspended Solid Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTA01BQ305XQ01 | BLDN DRAIN SURGE TK B AIT (COND) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 532 | μs/cm | 0 | 600 | μs/cm | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Conductivity Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTA01BQ306XQ01 | BLDN DRAIN SURGE TK B AIT (PH) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 14 | pH | 0 | 14 | pH | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | PH Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTA01BT301XQ01 | BLDN DRAIN SURGE TK A TIT | D-AI | 4-20mA | S | - | 65 | - | - | ℃ | NO | YES | - | - | - | 0 | 120 | ℃ | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00GTA01BT302XQ01 | BLDN DRAIN SURGE TK B TIT | D-AI | 4-20mA | S | - | 65 | - | - | ℃ | NO | YES | - | - | - | 0 | 120 | ℃ | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00GTA01GP501XB01 | BLDN DRAIN FEED PPS A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | MCC | DCDAS | - | - | -
=C00GTA01GP501XB49 | BLDN DRAIN FEED PPS A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | MCC | DCDAS | - | - | -
=C00GTA01GP501XB50 | BLDN DRAIN FEED PPS A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | MCC | DCDAS | - | - | -
=C00GTA01GP501XB61 | BLDN DRAIN FEED PPS A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | DCDAS | MCC | - | - | -
=C00GTA01GP501XB62 | BLDN DRAIN FEED PPS A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | DCDAS | MCC | - | - | -
=C00GTA01GP501XB69 | BLDN DRAIN FEED PPS A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | DCDAS | MCC | - | - | -
=C00GTA01GP501XB78 | BLDN DRAIN FEED PPS A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | MCC | DCDAS | - | - | -
=C00GTA01GP511XB01 | BLDN DRAIN FEED PPS B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | MCC | DCDAS | - | - | -
=C00GTA01GP511XB49 | BLDN DRAIN FEED PPS B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | MCC | DCDAS | - | - | -
=C00GTA01GP511XB50 | BLDN DRAIN FEED PPS B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | MCC | DCDAS | - | - | -
=C00GTA01GP511XB61 | BLDN DRAIN FEED PPS B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | DCDAS | MCC | - | - | -
=C00GTA01GP511XB62 | BLDN DRAIN FEED PPS B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | DCDAS | MCC | - | - | -
=C00GTA01GP511XB69 | BLDN DRAIN FEED PPS B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | DCDAS | MCC | - | - | -
=C00GTA01GP511XB78 | BLDN DRAIN FEED PPS B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6601 | - | MCC | DCDAS | - | - | -
=C00GTB41BF301XQ01 | FILTER A INL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB41BF302XQ01 | BACKWASH WTR PP OUTLET FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | HOLD | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB41BP001XG01 | FILTER A PDIS H | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | D/P Pressure Switch Diaphragm Type with indicator | FIELD | DCDAS | - | - | -
=C00GTB41QM081XB01 | FR BLDN DRAIN FEED PP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM081XB02 | FR BLDN DRAIN FEED PP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM081XB20 | FR BLDN DRAIN FEED PP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM081XB49 | FR BLDN DRAIN FEED PP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM081XB50 | FR BLDN DRAIN FEED PP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM081XB61 | FR BLDN DRAIN FEED PP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM081XB62 | FR BLDN DRAIN FEED PP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM081XB63 | FR BLDN DRAIN FEED PP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM081XB64 | FR BLDN DRAIN FEED PP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM081XB87 | FR BLDN DRAIN FEED PP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM081XB88 | FR BLDN DRAIN FEED PP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM081XG33 | FR BLDN DRAIN FEED PP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM081XG34 | FR BLDN DRAIN FEED PP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM082XB01 | TO BACKWASH WTR SUMP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM082XB02 | TO BACKWASH WTR SUMP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM082XB20 | TO BACKWASH WTR SUMP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM082XB49 | TO BACKWASH WTR SUMP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM082XB50 | TO BACKWASH WTR SUMP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM082XB61 | TO BACKWASH WTR SUMP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM082XB62 | TO BACKWASH WTR SUMP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM082XB63 | TO BACKWASH WTR SUMP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM082XB64 | TO BACKWASH WTR SUMP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM082XB87 | TO BACKWASH WTR SUMP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM082XB88 | TO BACKWASH WTR SUMP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM082XG33 | TO BACKWASH WTR SUMP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM082XG34 | TO BACKWASH WTR SUMP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM083XB01 | FR BACKWASH WTR PP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM083XB02 | FR BACKWASH WTR PP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM083XB20 | FR BACKWASH WTR PP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM083XB49 | FR BACKWASH WTR PP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM083XB50 | FR BACKWASH WTR PP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM083XB61 | FR BACKWASH WTR PP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM083XB62 | FR BACKWASH WTR PP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM083XB63 | FR BACKWASH WTR PP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM083XB64 | FR BACKWASH WTR PP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM083XB87 | FR BACKWASH WTR PP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM083XB88 | FR BACKWASH WTR PP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM083XG33 | FR BACKWASH WTR PP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM083XG34 | FR BACKWASH WTR PP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM084XB01 | TO L-P WWT SUMP FOR RWTS MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM084XB02 | TO L-P WWT SUMP FOR RWTS MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM084XB20 | TO L-P WWT SUMP FOR RWTS MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM084XB49 | TO L-P WWT SUMP FOR RWTS MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM084XB50 | TO L-P WWT SUMP FOR RWTS MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM084XB61 | TO L-P WWT SUMP FOR RWTS MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM084XB62 | TO L-P WWT SUMP FOR RWTS MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM084XB63 | TO L-P WWT SUMP FOR RWTS MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM084XB64 | TO L-P WWT SUMP FOR RWTS MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM084XB87 | TO L-P WWT SUMP FOR RWTS MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM084XB88 | TO L-P WWT SUMP FOR RWTS MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM084XG33 | TO L-P WWT SUMP FOR RWTS MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM084XG34 | TO L-P WWT SUMP FOR RWTS MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM085XB01 | FILTER A INL FLOW MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM085XB02 | FILTER A INL FLOW MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM085XB20 | FILTER A INL FLOW MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM085XB49 | FILTER A INL FLOW MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM085XB50 | FILTER A INL FLOW MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM085XB61 | FILTER A INL FLOW MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM085XB62 | FILTER A INL FLOW MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM085XB63 | FILTER A INL FLOW MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM085XB64 | FILTER A INL FLOW MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM085XB87 | FILTER A INL FLOW MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM085XB88 | FILTER A INL FLOW MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM085XG33 | FILTER A INL FLOW MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM085XG34 | FILTER A INL FLOW MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM086XB01 | FILTER A OUTL FLOW MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM086XB02 | FILTER A OUTL FLOW MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM086XB20 | FILTER A OUTL FLOW MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM086XB49 | FILTER A OUTL FLOW MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM086XB50 | FILTER A OUTL FLOW MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM086XB61 | FILTER A OUTL FLOW MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM086XB62 | FILTER A OUTL FLOW MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM086XB63 | FILTER A OUTL FLOW MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM086XB64 | FILTER A OUTL FLOW MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM086XB87 | FILTER A OUTL FLOW MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM086XB88 | FILTER A OUTL FLOW MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM086XG33 | FILTER A OUTL FLOW MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM086XG34 | FILTER A OUTL FLOW MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM087XB01 | TO FILTER A MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM087XB02 | TO FILTER A MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM087XB20 | TO FILTER A MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM087XB49 | TO FILTER A MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM087XB50 | TO FILTER A MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB41QM087XB61 | TO FILTER A MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM087XB62 | TO FILTER A MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB41QM087XB63 | TO FILTER A MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM087XB64 | TO FILTER A MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB41QM087XB87 | TO FILTER A MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM087XB88 | TO FILTER A MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM087XG33 | TO FILTER A MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB41QM087XG34 | TO FILTER A MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42BF301XQ01 | FILTER B INL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB42BF302XQ01 | BACKWASH WTR PP OUTLET FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | HOLD | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB42BP001XG01 | FILTER B PDIS H | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | D/P Pressure Switch Diaphragm Type with indicator | FIELD | DCDAS | - | - | -
=C00GTB42QM081XB01 | FR BLDN DRAIN FEED PP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM081XB02 | FR BLDN DRAIN FEED PP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM081XB20 | FR BLDN DRAIN FEED PP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM081XB49 | FR BLDN DRAIN FEED PP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM081XB50 | FR BLDN DRAIN FEED PP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM081XB61 | FR BLDN DRAIN FEED PP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM081XB62 | FR BLDN DRAIN FEED PP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM081XB63 | FR BLDN DRAIN FEED PP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM081XB64 | FR BLDN DRAIN FEED PP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM081XB87 | FR BLDN DRAIN FEED PP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM081XB88 | FR BLDN DRAIN FEED PP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM081XG33 | FR BLDN DRAIN FEED PP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM081XG34 | FR BLDN DRAIN FEED PP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM082XB01 | TO BACKWASH WTR SUMP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM082XB02 | TO BACKWASH WTR SUMP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM082XB20 | TO BACKWASH WTR SUMP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM082XB49 | TO BACKWASH WTR SUMP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM082XB50 | TO BACKWASH WTR SUMP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM082XB61 | TO BACKWASH WTR SUMP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM082XB62 | TO BACKWASH WTR SUMP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM082XB63 | TO BACKWASH WTR SUMP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM082XB64 | TO BACKWASH WTR SUMP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM082XB87 | TO BACKWASH WTR SUMP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM082XB88 | TO BACKWASH WTR SUMP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM082XG33 | TO BACKWASH WTR SUMP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM082XG34 | TO BACKWASH WTR SUMP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM083XB01 | FR BACKWASH WTR PP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM083XB02 | FR BACKWASH WTR PP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM083XB20 | FR BACKWASH WTR PP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM083XB49 | FR BACKWASH WTR PP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM083XB50 | FR BACKWASH WTR PP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM083XB61 | FR BACKWASH WTR PP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM083XB62 | FR BACKWASH WTR PP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM083XB63 | FR BACKWASH WTR PP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM083XB64 | FR BACKWASH WTR PP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM083XB87 | FR BACKWASH WTR PP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM083XB88 | FR BACKWASH WTR PP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM083XG33 | FR BACKWASH WTR PP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM083XG34 | FR BACKWASH WTR PP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM084XB01 | TO L-P WWT SUMP FOR RWTS MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM084XB02 | TO L-P WWT SUMP FOR RWTS MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM084XB20 | TO L-P WWT SUMP FOR RWTS MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM084XB49 | TO L-P WWT SUMP FOR RWTS MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM084XB50 | TO L-P WWT SUMP FOR RWTS MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM084XB61 | TO L-P WWT SUMP FOR RWTS MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM084XB62 | TO L-P WWT SUMP FOR RWTS MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM084XB63 | TO L-P WWT SUMP FOR RWTS MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM084XB64 | TO L-P WWT SUMP FOR RWTS MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM084XB87 | TO L-P WWT SUMP FOR RWTS MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM084XB88 | TO L-P WWT SUMP FOR RWTS MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM084XG33 | TO L-P WWT SUMP FOR RWTS MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM084XG34 | TO L-P WWT SUMP FOR RWTS MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM085XB01 | FILTER B INL FLOW MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM085XB02 | FILTER B INL FLOW MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM085XB20 | FILTER B INL FLOW MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM085XB49 | FILTER B INL FLOW MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM085XB50 | FILTER B INL FLOW MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM085XB61 | FILTER B INL FLOW MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM085XB62 | FILTER B INL FLOW MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM085XB63 | FILTER B INL FLOW MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM085XB64 | FILTER B INL FLOW MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM085XB87 | FILTER B INL FLOW MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM085XB88 | FILTER B INL FLOW MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM085XG33 | FILTER B INL FLOW MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM085XG34 | FILTER B INL FLOW MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM086XB01 | FILTER B OUTL FLOW MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM086XB02 | FILTER B OUTL FLOW MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM086XB20 | FILTER B OUTL FLOW MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM086XB49 | FILTER B OUTL FLOW MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM086XB50 | FILTER B OUTL FLOW MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM086XB61 | FILTER B OUTL FLOW MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM086XB62 | FILTER B OUTL FLOW MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM086XB63 | FILTER B OUTL FLOW MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM086XB64 | FILTER B OUTL FLOW MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM086XB87 | FILTER B OUTL FLOW MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM086XB88 | FILTER B OUTL FLOW MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM086XG33 | FILTER B OUTL FLOW MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM086XG34 | FILTER B OUTL FLOW MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM087XB01 | TO FILTER B MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM087XB02 | TO FILTER B MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM087XB20 | TO FILTER B MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM087XB49 | TO FILTER B MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM087XB50 | TO FILTER B MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB42QM087XB61 | TO FILTER B MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM087XB62 | TO FILTER B MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB42QM087XB63 | TO FILTER B MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM087XB64 | TO FILTER B MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB42QM087XB87 | TO FILTER B MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM087XB88 | TO FILTER B MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM087XG33 | TO FILTER B MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB42QM087XG34 | TO FILTER B MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6602 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01BF301XQ01 | FR HX FEED PPS TO RECL WTR TK FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 60 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BL001XG01 | BACKWASH WTR SUMPLSH | D-DI | 24VDC | S | - | 5670 | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTB01BL001XG03 | BACKWASH WTR SUMP LSHH | D-DI | 24VDC | S | 5985 | - | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTB01BL001XG52 | BACKWASH WTR SUMP LSL | D-DI | 24VDC | S | - | - | 2100 | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTB01BL001XG54 | BACKWASH WTR SUMP LSLL | D-DI | 24VDC | S | - | - | - | 630 | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTB01BL301XQ01 | BACKWASH WTR SUMP LIT | D-AI | 4-20mA | S | 5985 | 5670 | 2100 | 630 | mm | NO | YES | - | - | - | 200 | 6500 | mm | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Radar Level Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BP001XG52 | HX FEED PP OUTL PSH | D-DI | 24VDC | S | - | - | 0.36 | - | MPaG | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Pressure Switch | FIELD | DCDAS | - | - | -
=C00GTB01BP002XG52 | BACKWASH WTR PP OUTL PSH | D-DI | 24VDC | S | - | - | 0.24 | - | MPaG | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Pressure Switch | FIELD | DCDAS | - | - | -
=C00GTB01BP301XQ01 | HX FEED PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTB01BP302XQ01 | HX FEED PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTB01BP304XQ01 | BACKWASH WTR PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTB01BP305XQ01 | BACKWASH WTR PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTB01BQ301XQ01 | BACKWASH WTR SUMP AIT (SS) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 2 | mg/L | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Suspended Solid Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTB01BQ302XQ01 | BACKWASH WTR SUMP AIT (TURB) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 5 | NTU | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Turbidity Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTB01BQ303XQ01 | BACKWASH WTR SUMP AIT (COND) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 532 | μs/cm | 0 | 600 | μs/cm | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Conductivity Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTB01BQ304XQ01 | BACKWASH WTR SUMP AIT (PH) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 14 | pH | 0 | 14 | pH | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | PH Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTB01BT301XQ01 | BACKWASH WTR SUMP TIT | D-AI | 4-20mA | S | - | 65 | - | - | ℃ | NO | YES | - | - | - | 0 | 120 | ℃ | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01GP501XB01 | HX FEED PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP501XB49 | HX FEED PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP501XB50 | HX FEED PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP501XB61 | HX FEED PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP501XB62 | HX FEED PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP501XB69 | HX FEED PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP501XB78 | HX FEED PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP502XB01 | BACKWASH WTR PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP502XB49 | BACKWASH WTR PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP502XB50 | BACKWASH WTR PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP502XB61 | BACKWASH WTR PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP502XB62 | BACKWASH WTR PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP502XB69 | BACKWASH WTR PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP502XB78 | BACKWASH WTR PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP511XB01 | HX FEED PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP511XB49 | HX FEED PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP511XB50 | HX FEED PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP511XB61 | HX FEED PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP511XB62 | HX FEED PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP511XB69 | HX FEED PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP511XB78 | HX FEED PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP512XB01 | BACKWASH WTR PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP512XB49 | BACKWASH WTR PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP512XB50 | BACKWASH WTR PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01GP512XB61 | BACKWASH WTR PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP512XB62 | BACKWASH WTR PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP512XB69 | BACKWASH WTR PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | DCDAS | MCC | - | - | -
=C00GTB01GP512XB78 | BACKWASH WTR PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | - | MCC | DCDAS | - | - | -
=C00GTB01QM081XB01 | FR HX FEED PPS MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM081XB02 | FR HX FEED PPS MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM081XB20 | FR HX FEED PPS MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM081XB49 | FR HX FEED PPS MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM081XB50 | FR HX FEED PPS MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM081XB61 | FR HX FEED PPS MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM081XB62 | FR HX FEED PPS MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM081XB63 | FR HX FEED PPS MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM081XB64 | FR HX FEED PPS MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM081XB87 | FR HX FEED PPS MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM081XB88 | FR HX FEED PPS MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM081XG33 | FR HX FEED PPS MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM081XG34 | FR HX FEED PPS MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6603 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GAF01BF371XQ01 | TO HX FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 250 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BP071XG52 | TO HX PS L | D-DI | 24VDC | S | - | - | 0.43 | - | MPaG | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GAF01BP371XQ01 | HX COOLING WTR SPLY PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GAF01BP372XQ01 | HX COOLING WTR SPLY PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GAF01BP373XQ01 | TO HX PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 0.906 | MPaG | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GAF01BP374XQ01 | FR HX TO RAW WTR BUFF TK PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 0.77 | MPaG | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GAF01BT371XQ01 | TO HX TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 100 | ℃ | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01BT372XQ01 | FR HX TO RAW WTR BUFF TK TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 100 | ℃ | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00GAF01GP504XB01 | HX COOLING WTR SPLY PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | MCC | DCDAS | - | - | -
=C00GAF01GP504XB49 | HX COOLING WTR SPLY PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | MCC | DCDAS | - | - | -
=C00GAF01GP504XB50 | HX COOLING WTR SPLY PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | MCC | DCDAS | - | - | -
=C00GAF01GP504XB61 | HX COOLING WTR SPLY PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | DCDAS | MCC | - | - | -
=C00GAF01GP504XB62 | HX COOLING WTR SPLY PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | DCDAS | MCC | - | - | -
=C00GAF01GP504XB69 | HX COOLING WTR SPLY PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | DCDAS | MCC | - | - | -
=C00GAF01GP504XB78 | HX COOLING WTR SPLY PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | MCC | DCDAS | - | - | -
=C00GAF01GP514XB01 | HX COOLING WTR SPLY PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | MCC | DCDAS | - | - | -
=C00GAF01GP514XB49 | HX COOLING WTR SPLY PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | MCC | DCDAS | - | - | -
=C00GAF01GP514XB50 | HX COOLING WTR SPLY PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | MCC | DCDAS | - | - | -
=C00GAF01GP514XB61 | HX COOLING WTR SPLY PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | DCDAS | MCC | - | - | -
=C00GAF01GP514XB62 | HX COOLING WTR SPLY PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | DCDAS | MCC | - | - | -
=C00GAF01GP514XB69 | HX COOLING WTR SPLY PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | DCDAS | MCC | - | - | -
=C00GAF01GP514XB78 | HX COOLING WTR SPLY PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | - | MCC | DCDAS | - | - | -
=C00GAF01QN001XG01 | FR HX COOLING WTR SPLY PP CV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00GAF01QN001XG02 | FR HX COOLING WTR SPLY PP CV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00GAF01QN001XQ01 | FR HX COOLING WTR SPLY PP CV-ZT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Globe Type Control Valve | FIELD | DCDAS | - | - | -
=C00GAF01QN001XQ23 | FR HX COOLING WTR SPLY PP CV-PY | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Globe Type Control Valve | DCDAS | FIELD | - | - | -
=C00GTB01BF302XQ01 | FR HX TO RECL WTR TK FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 60 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BF303XB27 | TO RAW WTR BUFF TK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 60 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BF303XQ01 | TO RAW WTR BUFF TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 60 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BP307XQ01 | FR HX FEED PP TO HX PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 0.772 | MPaG | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTB01BP308XQ01 | HX OUTL PIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 0.632 | MPaG | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTB01BT302XQ01 | FR HX FEED PP TO HX TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 120 | ℃ | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BT303XQ01 | HX OUTL TIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 120 | ℃ | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Temperature Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01QM082XB01 | FR HX FEED PP TO HX MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM082XB02 | FR HX FEED PP TO HX MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM082XB20 | FR HX FEED PP TO HX MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM082XB49 | FR HX FEED PP TO HX MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM082XB50 | FR HX FEED PP TO HX MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM082XB61 | FR HX FEED PP TO HX MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM082XB62 | FR HX FEED PP TO HX MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM082XB63 | FR HX FEED PP TO HX MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM082XB64 | FR HX FEED PP TO HX MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM082XB87 | FR HX FEED PP TO HX MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM082XB88 | FR HX FEED PP TO HX MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM082XG33 | FR HX FEED PP TO HX MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM082XG34 | FR HX FEED PP TO HX MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM083XB01 | FR HX TO RECL WTR TK MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM083XB02 | FR HX TO RECL WTR TK MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM083XB20 | FR HX TO RECL WTR TK MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM083XB49 | FR HX TO RECL WTR TK MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM083XB50 | FR HX TO RECL WTR TK MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM083XB61 | FR HX TO RECL WTR TK MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM083XB62 | FR HX TO RECL WTR TK MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM083XB63 | FR HX TO RECL WTR TK MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM083XB64 | FR HX TO RECL WTR TK MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM083XB87 | FR HX TO RECL WTR TK MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM083XB88 | FR HX TO RECL WTR TK MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM083XG33 | FR HX TO RECL WTR TK MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM083XG34 | FR HX TO RECL WTR TK MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM084XB01 | FR HX TO RAW WTR BUFF TK MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM084XB02 | FR HX TO RAW WTR BUFF TK MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM084XB20 | FR HX TO RAW WTR BUFF TK MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM084XB49 | FR HX TO RAW WTR BUFF TK MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM084XB50 | FR HX TO RAW WTR BUFF TK MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM084XB61 | FR HX TO RAW WTR BUFF TK MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM084XB62 | FR HX TO RAW WTR BUFF TK MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM084XB63 | FR HX TO RAW WTR BUFF TK MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM084XB64 | FR HX TO RAW WTR BUFF TK MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM084XB87 | FR HX TO RAW WTR BUFF TK MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM084XB88 | FR HX TO RAW WTR BUFF TK MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM084XG33 | FR HX TO RAW WTR BUFF TK MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM084XG34 | FR HX TO RAW WTR BUFF TK MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM085XB01 | FR HX TO BACKWASH WTR SUMP MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM085XB02 | FR HX TO BACKWASH WTR SUMP MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM085XB20 | FR HX TO BACKWASH WTR SUMP MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM085XB49 | FR HX TO BACKWASH WTR SUMP MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM085XB50 | FR HX TO BACKWASH WTR SUMP MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM085XB61 | FR HX TO BACKWASH WTR SUMP MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM085XB62 | FR HX TO BACKWASH WTR SUMP MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM085XB63 | FR HX TO BACKWASH WTR SUMP MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM085XB64 | FR HX TO BACKWASH WTR SUMP MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM085XB87 | FR HX TO BACKWASH WTR SUMP MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM085XB88 | FR HX TO BACKWASH WTR SUMP MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM085XG33 | FR HX TO BACKWASH WTR SUMP MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM085XG34 | FR HX TO BACKWASH WTR SUMP MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6604 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01BF304XB27 | TO DWTS FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 280 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BF304XQ01 | TO DWTS FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 280 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BF305XB27 | TO RAW WTR BUFF TK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 150 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BF305XQ01 | TO RAW WTR BUFF TK FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 150 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BL002XG01 | RECL WTR TK LSH | D-DI | 24VDC | S | - | 14850 | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTB01BL002XG03 | RECL WTR TK LSHH | D-DI | 24VDC | S | 15675 | - | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTB01BL002XG52 | RECL WTR TK LSL | D-DI | 24VDC | S | - | - | 1650 | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTB01BL002XG54 | RECL WTR TK LSLL | D-DI | 24VDC | S | - | - | - | 825 | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTB01BL302XQ01 | RECL WTR TK LIT | D-AI | 4-20mA | S | 15675 | 14850 | 1650 | 825 | mm | NO | YES | - | - | - | 0 | 16219 | mmH2O | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C00GTB01BP003XG52 | RECL WTR TRANS PPS OUTL PSL | D-DI | 24VDC | S | - | - | 0.25 | - | MPaG | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTB01BP309XQ01 | RECL WTR TRANS PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTB01BP310XQ01 | RECL WTR TRANS PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTB01BQ305XQ01 | RECL WTR TK AIT (COND) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 532 | μs/cm | 0 | 600 | μs/cm | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Conductivity Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTB01BQ306XQ01 | RECL WTR TK AIT (PH) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 14 | pH | 0 | 14 | pH | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | PH Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTB01BQ307XQ01 | RECL WTR TK AIT (SS) | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 2 | mg/L | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Suspended Solid Analyzer (Transmitter) | FIELD | DCDAS | - | - | -
=C00GTB01BT001XG01 | RECL WTR TK TSH | D-DI | 24VDC | S | - | 45 | - | - | ℃ | YES | NO | 0 | 100 | ℃ | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Temperature Switch | FIELD | DCDAS | - | - | -
=C00GTB01GP503XB01 | RECL WTR TRANS PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | MCC | DCDAS | - | - | -
=C00GTB01GP503XB49 | RECL WTR TRANS PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | MCC | DCDAS | - | - | -
=C00GTB01GP503XB50 | RECL WTR TRANS PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | MCC | DCDAS | - | - | -
=C00GTB01GP503XB61 | RECL WTR TRANS PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | DCDAS | MCC | - | - | -
=C00GTB01GP503XB62 | RECL WTR TRANS PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | DCDAS | MCC | - | - | -
=C00GTB01GP503XB69 | RECL WTR TRANS PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | DCDAS | MCC | - | - | -
=C00GTB01GP503XB78 | RECL WTR TRANS PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | MCC | DCDAS | - | - | -
=C00GTB01GP513XB01 | RECL WTR TRANS PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | MCC | DCDAS | - | - | -
=C00GTB01GP513XB49 | RECL WTR TRANS PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | MCC | DCDAS | - | - | -
=C00GTB01GP513XB50 | RECL WTR TRANS PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | MCC | DCDAS | - | - | -
=C00GTB01GP513XB61 | RECL WTR TRANS PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | DCDAS | MCC | - | - | -
=C00GTB01GP513XB62 | RECL WTR TRANS PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | DCDAS | MCC | - | - | -
=C00GTB01GP513XB69 | RECL WTR TRANS PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | DCDAS | MCC | - | - | -
=C00GTB01GP513XB78 | RECL WTR TRANS PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | - | MCC | DCDAS | - | - | -
=C00GTB01QM086XB01 | TO DWTS MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM086XB02 | TO DWTS MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM086XB20 | TO DWTS MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM086XB49 | TO DWTS MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM086XB50 | TO DWTS MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM086XB61 | TO DWTS MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM086XB62 | TO DWTS MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM086XB63 | TO DWTS MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM086XB64 | TO DWTS MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM086XB87 | TO DWTS MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM086XB88 | TO DWTS MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM086XG33 | TO DWTS MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM086XG34 | TO DWTS MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM087XB01 | TO RAW WTR BUFF TK MOV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM087XB02 | TO RAW WTR BUFF TK MOV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM087XB20 | TO RAW WTR BUFF TK MOV-LOC SEL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM087XB49 | TO RAW WTR BUFF TK MOV-ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM087XB50 | TO RAW WTR BUFF TK MOV-PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | MCC | DCDAS | - | - | -
=C00GTB01QM087XB61 | TO RAW WTR BUFF TK MOV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM087XB62 | TO RAW WTR BUFF TK MOV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | DCDAS | MCC | - | - | -
=C00GTB01QM087XB63 | TO RAW WTR BUFF TK MOV-OPN LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM087XB64 | TO RAW WTR BUFF TK MOV-CLS LAMP | D-DO | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GTB01QM087XB87 | TO RAW WTR BUFF TK MOV-OPN TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM087XB88 | TO RAW WTR BUFF TK MOV-CLS TORQ | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM087XG33 | TO RAW WTR BUFF TK MOV-OPN PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GTB01QM087XG34 | TO RAW WTR BUFF TK MOV-CLS PB ON | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6605 | Moter Operated Control Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C10GTA01BF301XQ01 | RECOV WTR PP FOR U1 SPL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 8 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | HOLD | TC0-1-UWM02-D6606 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GTA01BL001XG01 | RECOV WTR SUMP FOR U1 SPL LSH | D-DI | 24VDC | S | - | 1600 | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | Sump Pump Float Level Switch | FIELD | DCDAS | - | - | -
=C10GTA01BL001XG03 | RECOV WTR SUMP FOR U1 SPL LSHH | D-DI | 24VDC | S | 1900 | - | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | Sump Pump Float Level Switch | FIELD | DCDAS | - | - | -
=C10GTA01BL001XG52 | RECOV WTR SUMP FOR U1 SPL LSL | D-DI | 24VDC | S | - | - | 300 | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | Sump Pump Float Level Switch | FIELD | DCDAS | - | - | -
=C10GTA01BL001XG54 | RECOV WTR SUMP FOR U1 SPL LSLL | D-DI | 24VDC | S | - | - | - | 0 | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | Sump Pump Float Level Switch | FIELD | DCDAS | - | - | -
=C10GTA01CL001XB40 | RECOV WTR PP FOR U1 SPL CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C10GTA01GP501XB01 | RECOV WTR PP A FOR U1 SPL ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C10GTA01GP501XB49 | RECOV WTR PP A FOR U1 SPL ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C10GTA01GP501XB50 | RECOV WTR PP A FOR U1 SPL PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C10GTA01GP501XB61 | RECOV WTR PP A FOR U1 SPL ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C10GTA01GP501XB62 | RECOV WTR PP A FOR U1 SPL OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C10GTA01GP501XB69 | RECOV WTR PP A FOR U1 SPL STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C10GTA01GP501XB78 | RECOV WTR PP A FOR U1 SPL REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C10GTA01GP511XB01 | RECOV WTR PP B FOR U1 SPL ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C10GTA01GP511XB49 | RECOV WTR PP B FOR U1 SPL ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C10GTA01GP511XB50 | RECOV WTR PP B FOR U1 SPL PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C10GTA01GP511XB61 | RECOV WTR PP B FOR U1 SPL ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C10GTA01GP511XB62 | RECOV WTR PP B FOR U1 SPL OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C10GTA01GP511XB69 | RECOV WTR PP B FOR U1 SPL STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C10GTA01GP511XB78 | RECOV WTR PP B FOR U1 SPL REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST1 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C20GTA01BF301XQ01 | RECOV WTR PP FOR U2 SPL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 8 | m3/hr | RECOVERY WATER TREATMENT SYSTEM (COMMON) | HOLD | TC0-1-UWM02-D6606 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GTA01BL001XG01 | RECOV WTR SUMP FOR U2 SPL LSH | D-DI | 24VDC | S | - | 1600 | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | Sump Pump Float Level Switch | FIELD | DCDAS | - | - | -
=C20GTA01BL001XG03 | RECOV WTR SUMP FOR U2 SPL LSHH | D-DI | 24VDC | S | 1900 | - | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | Sump Pump Float Level Switch | FIELD | DCDAS | - | - | -
=C20GTA01BL001XG52 | RECOV WTR SUMP FOR U2 SPL LSL | D-DI | 24VDC | S | - | - | 300 | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | Sump Pump Float Level Switch | FIELD | DCDAS | - | - | -
=C20GTA01BL001XG54 | RECOV WTR SUMP FOR U2 SPL LSLL | D-DI | 24VDC | S | - | - | - | 0 | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | Sump Pump Float Level Switch | FIELD | DCDAS | - | - | -
=C20GTA01CL001XB40 | RECOV WTR PP FOR U2 SPL CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C20GTA01GP501XB01 | RECOV WTR PP A FOR U2 SPL ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C20GTA01GP501XB49 | RECOV WTR PP A FOR U2 SPL ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C20GTA01GP501XB50 | RECOV WTR PP A FOR U2 SPL PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C20GTA01GP501XB61 | RECOV WTR PP A FOR U2 SPL ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C20GTA01GP501XB62 | RECOV WTR PP A FOR U2 SPL OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C20GTA01GP501XB69 | RECOV WTR PP A FOR U2 SPL STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C20GTA01GP501XB78 | RECOV WTR PP A FOR U2 SPL REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C20GTA01GP511XB01 | RECOV WTR PP B FOR U2 SPL ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C20GTA01GP511XB49 | RECOV WTR PP B FOR U2 SPL ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C20GTA01GP511XB50 | RECOV WTR PP B FOR U2 SPL PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C20GTA01GP511XB61 | RECOV WTR PP B FOR U2 SPL ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C20GTA01GP511XB62 | RECOV WTR PP B FOR U2 SPL OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C20GTA01GP511XB69 | RECOV WTR PP B FOR U2 SPL STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | DCDAS | MCC | - | - | -
=C20GTA01GP511XB78 | RECOV WTR PP B FOR U2 SPL REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | ST2 | TC0-1-UWM02-D6606 | - | MCC | DCDAS | - | - | -
=C00GTA01BL003XG01 | RECOV WTR SUMP FOR DWTS LSH | D-DI | 24VDC | S | - | 2550 | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL003XG03 | RECOV WTR SUMP FOR DWTS LSHH | D-DI | 24VDC | S | 2700 | - | - | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL003XG52 | RECOV WTR SUMP FOR DWTS LSL | D-DI | 24VDC | S | - | - | 300 | - | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL003XG54 | RECOV WTR SUMP FOR DWTS LSLL | D-DI | 24VDC | S | - | - | - | 0 | mm | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GTA01BL303XQ01 | RECOV WTR SUMP FOR DWTS LIT | D-AI | 4-20mA | S | 2700 | 2550 | 300 | - | mm | NO | YES | - | - | - | 200 | 5000 | mm | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | Radar Level Transmitter | FIELD | DCDAS | - | - | -
=C00GTA01BP001XG52 | RECOV WTR PPS FOR DWTS OUTL PS L | D-DI | 24VDC | S | - | - | 0.17 | - | MPaG | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | Pressure Switch Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTA01BP304XQ01 | RECOV WTR PP FOR DWTS A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTA01BP305XQ01 | RECOV WTR PP FOR DWTS B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GTA01GP502XB01 | RECOV WTR PP A FOR DWTS ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | MCC | DCDAS | - | - | -
=C00GTA01GP502XB49 | RECOV WTR PP A FOR DWTS ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | MCC | DCDAS | - | - | -
=C00GTA01GP502XB50 | RECOV WTR PP A FOR DWTS PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | MCC | DCDAS | - | - | -
=C00GTA01GP502XB61 | RECOV WTR PP A FOR DWTS ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | DCDAS | MCC | - | - | -
=C00GTA01GP502XB62 | RECOV WTR PP A FOR DWTS OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | DCDAS | MCC | - | - | -
=C00GTA01GP502XB69 | RECOV WTR PP A FOR DWTS STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | DCDAS | MCC | - | - | -
=C00GTA01GP502XB78 | RECOV WTR PP A FOR DWTS REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | MCC | DCDAS | - | - | -
=C00GTA01GP512XB01 | RECOV WTR PP B FOR DWTS ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | MCC | DCDAS | - | - | -
=C00GTA01GP512XB49 | RECOV WTR PP B FOR DWTS ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | MCC | DCDAS | - | - | -
=C00GTA01GP512XB50 | RECOV WTR PP B FOR DWTS PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | MCC | DCDAS | - | - | -
=C00GTA01GP512XB61 | RECOV WTR PP B FOR DWTS ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | DCDAS | MCC | - | - | -
=C00GTA01GP512XB62 | RECOV WTR PP B FOR DWTS OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | DCDAS | MCC | - | - | -
=C00GTA01GP512XB69 | RECOV WTR PP B FOR DWTS STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | DCDAS | MCC | - | - | -
=C00GTA01GP512XB78 | RECOV WTR PP B FOR DWTS REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | RECOVERY WATER TREATMENT SYSTEM (COMMON) | DWT | TC0-1-UWM02-D6607 | - | MCC | DCDAS | - | - | -
=C00PHB01BF301XB27 | TO AWWT SYS FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 50 | m3/hr | SERVICE WATER SYSTEM (COMMON) | WWT | TC0-1-USM02-D6001 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00PHB01BF301XQ01 | TO AWWT SYS FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 50 | m3/hr | SERVICE WATER SYSTEM (COMMON) | WWT | TC0-1-USM02-D6001 | Vortex Flow Transmitter | FIELD | DCDAS | - | - | -
=C00PHB01BP301XQ01 | TO AWWTS PIT | D-AI | 4-20mA | S | - | - | - | 0.042 | MPaG | NO | YES | - | - | - | 0 | 0.94 | MPaG | SERVICE WATER SYSTEM (COMMON) | WWT | TC0-1-USM02-D6001 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00PHB01BP302XQ01 | TO AWWT SYS PIT | D-AI | 4-20mA | S | - | - | 0.698 | - | MPaG | NO | YES | - | - | - | 0 | 1.47 | MPaG | SERVICE WATER SYSTEM (COMMON) | WWT | TC0-1-USM02-D6001 | Pressure Transmitter | FIELD | DCDAS | - | - | -
=C00PHB01GP501XB01 | SVC WTR BSTR PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C00PHB01GP501XB49 | SVC WTR BSTR PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C00PHB01GP501XB50 | SVC WTR BSTR PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C00PHB01GP501XB61 | SVC WTR BSTR PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | DCDAS | EMCC | - | - | -
=C00PHB01GP501XB62 | SVC WTR BSTR PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | DCDAS | EMCC | - | - | -
=C00PHB01GP501XB69 | SVC WTR BSTR PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | DCDAS | EMCC | - | - | -
=C00PHB01GP501XB78 | SVC WTR BSTR PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C00PHB01GP501XQ01 | SVC WTR BSTR PP A AMP | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C00PHB01GP511XB01 | SVC WTR BSTR PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C00PHB01GP511XB49 | SVC WTR BSTR PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C00PHB01GP511XB50 | SVC WTR BSTR PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C00PHB01GP511XB61 | SVC WTR BSTR PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | DCDAS | EMCC | - | - | -
=C00PHB01GP511XB62 | SVC WTR BSTR PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | DCDAS | EMCC | - | - | -
=C00PHB01GP511XB69 | SVC WTR BSTR PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | DCDAS | EMCC | - | - | -
=C00PHB01GP511XB78 | SVC WTR BSTR PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C00PHB01GP511XQ01 | SVC WTR BSTR PP B AMP | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | SERVICE WATER SYSTEM (COMMON) | ST1 | TC0-1-USM02-D6001 | - | EMCC | DCDAS | - | - | -
=C10MVA01BL002XG01 | U1 DIRTY LUBE OIL STG TK LIS H | D-DI | 24VDC | S | - | 4860 | - | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10MVA01BL002XG52 | U1 DIRTY LUBE OIL STG TK LIS L | D-DI | 24VDC | S | - | - | 540 | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10MVA01BL004XG01 | U1 CLEAN LUBE OIL STG TK LIS H | D-DI | 24VDC | S | - | 4860 | - | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10MVA01BL004XG52 | U1 CLEAN LUBE OIL STG TK LIS L | D-DI | 24VDC | S | - | - | 540 | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10MVA01BL301XQ01 | U1 DIRTY LUBE OIL STG TK LIT | D-AI | 4-20mA | S | - | 4860 | 540 | - | mm | NO | YES | - | - | - | 0 | 4590 | mmH2O | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C10MVA01BL302XQ01 | U1 CLEAN LUBE OIL STG TK LIT | D-AI | 4-20mA | S | - | 4860 | 540 | - | mm | NO | YES | - | - | - | 0 | 4590 | mmH2O | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C10MVA01BP301XQ01 | U1 DIRTY STG OIL TRANS PP INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C10MVA01BP302XQ01 | U1 CLEAN STG OIL TRANS PP INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C10MVA01GP001XB01 | U1 DIRTY STG OIL TRANS PP ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C10MVA01GP001XB49 | U1 DIRTY STG OIL TRANS PP ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C10MVA01GP001XB50 | U1 DIRTY STG OIL TRANS PP PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C10MVA01GP001XB61 | U1 DIRTY STG OIL TRANS PP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C10MVA01GP001XB62 | U1 DIRTY STG OIL TRANS PP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C10MVA01GP001XB69 | U1 DIRTY STG OIL TRANS PP STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C10MVA01GP001XB78 | U1 DIRTY STG OIL TRANS PP REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C10MVA01GP002XB01 | U1 CLEAN STG OIL TRANS PP ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C10MVA01GP002XB49 | U1 CLEAN STG OIL TRANS PP ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C10MVA01GP002XB50 | U1 CLEAN STG OIL TRANS PP PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C10MVA01GP002XB61 | U1 CLEAN STG OIL TRANS PP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C10MVA01GP002XB62 | U1 CLEAN STG OIL TRANS PP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C10MVA01GP002XB69 | U1 CLEAN STG OIL TRANS PP STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C10MVA01GP002XB78 | U1 CLEAN STG OIL TRANS PP REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC1-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C10MVA01BL001XG01 | U1 DIRTY LUBE OIL STG TK LIS H | D-DI | 24VDC | S | - | 4800 | - | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC2-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C10MVA01BL003XG01 | U1 CLEAN LUBE OIL STG TK LIS H | D-DI | 24VDC | S | - | 4800 | - | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#1) | DWT | TC2-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20MVA01BL001XG01 | U2 DIRTY LUBE OIL STG TK LIS H | D-DI | 24VDC | S | - | 4800 | - | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20MVA01BL002XG01 | U2 DIRTY LUBE OIL STG TK LIS H | D-DI | 24VDC | S | - | 4860 | - | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20MVA01BL002XG52 | U2 DIRTY LUBE OIL STG TK LIS L | D-DI | 24VDC | S | - | - | 540 | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20MVA01BL003XG01 | U2 CLEAN LUBE OIL STG TK LIS H | D-DI | 24VDC | S | - | 4800 | - | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20MVA01BL004XG01 | U2 CLEAN LUBE OIL STG TK LIS H | D-DI | 24VDC | S | - | 4860 | - | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20MVA01BL004XG52 | U2 CLEAN LUBE OIL STG TK LIS L | D-DI | 24VDC | S | - | - | 540 | - | mm | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | Magnetic Level Gauge (w/switch) | FIELD | DCDAS | - | - | -
=C20MVA01BL301XQ01 | U2 DIRTY LUBE OIL STG TK LIT | D-AI | 4-20mA | S | - | 4860 | 540 | - | mm | NO | YES | - | - | - | 0 | 4590 | mmH2O | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C20MVA01BL302XQ01 | U2 CLEAN LUBE OIL STG TK LIT | D-AI | 4-20mA | S | - | 4860 | 540 | - | mm | NO | YES | - | - | - | 0 | 4590 | mmH2O | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | D/P Level Transmitter | FIELD | DCDAS | - | - | -
=C20MVA01BP301XQ01 | U2 DIRTY STG OIL TRANS PP INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C20MVA01BP302XQ01 | U2 CLEAN STG OIL TRANS PP INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C20MVA01GP001XB01 | U2 DIRTY STG OIL TRANS PP ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C20MVA01GP001XB49 | U2 DIRTY STG OIL TRANS PP ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C20MVA01GP001XB50 | U2 DIRTY STG OIL TRANS PP PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C20MVA01GP001XB61 | U2 DIRTY STG OIL TRANS PP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C20MVA01GP001XB62 | U2 DIRTY STG OIL TRANS PP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C20MVA01GP001XB69 | U2 DIRTY STG OIL TRANS PP STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C20MVA01GP001XB78 | U2 DIRTY STG OIL TRANS PP REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C20MVA01GP002XB01 | U2 CLEAN STG OIL TRANS PP ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C20MVA01GP002XB49 | U2 CLEAN STG OIL TRANS PP ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C20MVA01GP002XB50 | U2 CLEAN STG OIL TRANS PP PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C20MVA01GP002XB61 | U2 CLEAN STG OIL TRANS PP ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C20MVA01GP002XB62 | U2 CLEAN STG OIL TRANS PP OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C20MVA01GP002XB69 | U2 CLEAN STG OIL TRANS PP STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | DCDAS | MCC | - | - | -
=C20MVA01GP002XB78 | U2 CLEAN STG OIL TRANS PP REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | TURBINE OIL CONDITIONING SYSTEM (CC#2) | DWT | TC2-1-TGM02-D6001 | - | MCC | DCDAS | - | - | -
=C10GMV01BF301XB27 | H-P SUMP FOR U1 ST OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 25 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMV01BF301XQ01 | H-P SUMP FOR U1 ST OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 25 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMV01BF302XQ01 | H-P SUMP FOR U1 OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | HOLD | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMV01XD801AXB41 | H-P SUMP FOR U1 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD801AXJ51 | H-P SUMP FOR U1 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD801BXB41 | H-P SUMP FOR U1 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD801BXJ51 | H-P SUMP FOR U1 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD801XB40 | H-P SUMP FOR U1 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD801XG01 | H-P SUMP FOR U1 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD801XG03 | H-P SUMP FOR U1 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD801XG52 | H-P SUMP FOR U1 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD801XG54 | H-P SUMP FOR U1 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD802AXB41 | H-P SUMP FOR U1 ST PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD802AXJ51 | H-P SUMP FOR U1 ST PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD802BXB41 | H-P SUMP FOR U1 ST PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD802BXJ51 | H-P SUMP FOR U1 ST PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD802XB40 | H-P SUMP FOR U1 ST LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD802XG01 | H-P SUMP FOR U1 ST LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD802XG03 | H-P SUMP FOR U1 ST LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD802XG52 | H-P SUMP FOR U1 ST LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01XD802XG54 | H-P SUMP FOR U1 ST LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C10GMV01BF303XB27 | H-P SUMP FOR U1 ST2 OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 25 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMV01BF303XQ01 | H-P SUMP FOR U1 ST2 OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 25 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMV01XD803AXB41 | H-P SUMP FOR U1 ST2 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C10GMV01XD803AXJ51 | H-P SUMP FOR U1 ST2 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C10GMV01XD803BXB41 | H-P SUMP FOR U1 ST2 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C10GMV01XD803BXJ51 | H-P SUMP FOR U1 ST2 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C10GMV01XD803XB40 | H-P SUMP FOR U1 ST2 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C10GMV01XD803XG01 | H-P SUMP FOR U1 ST2 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C10GMV01XD803XG03 | H-P SUMP FOR U1 ST2 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C10GMV01XD803XG52 | H-P SUMP FOR U1 ST2 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C10GMV01XD803XG54 | H-P SUMP FOR U1 ST2 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C20GMV01BF301XB27 | H-P SUMP FOR U2 ST OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 25 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMV01BF301XQ01 | H-P SUMP FOR U2 ST OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 25 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMV01BF302XB27 | H-P SUMP FOR U2 OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMV01BF302XQ01 | H-P SUMP FOR U2 OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMV01XD801AXB41 | H-P SUMP FOR U2 ST PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD801AXJ51 | H-P SUMP FOR U2 ST PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD801BXB41 | H-P SUMP FOR U2 ST PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD801BXJ51 | H-P SUMP FOR U2 ST PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD801XB40 | H-P SUMP FOR U2 ST LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD801XG01 | H-P SUMP FOR U2 ST LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD801XG03 | H-P SUMP FOR U2 ST LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD801XG52 | H-P SUMP FOR U2 ST LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD801XG54 | H-P SUMP FOR U2 ST LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD802AXB41 | H-P SUMP FOR U2 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD802AXJ51 | H-P SUMP FOR U2 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD802BXB41 | H-P SUMP FOR U2 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD802BXJ51 | H-P SUMP FOR U2 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD802XB40 | H-P SUMP FOR U2 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD802XG01 | H-P SUMP FOR U2 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD802XG03 | H-P SUMP FOR U2 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD802XG52 | H-P SUMP FOR U2 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01XD802XG54 | H-P SUMP FOR U2 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C20GMV01BF303XB27 | H-P PP FOR U2 ST2 OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 25 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMV01BF303XQ01 | H-P PP FOR U2 ST2 OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 25 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMV01XD803AXB41 | H-P SUMP FOR U2 ST2 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C20GMV01XD803AXJ51 | H-P SUMP FOR U2 ST2 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C20GMV01XD803BXB41 | H-P SUMP FOR U2 ST2 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C20GMV01XD803BXJ51 | H-P SUMP FOR U2 ST2 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C20GMV01XD803XB40 | H-P SUMP FOR U2 ST2 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C20GMV01XD803XG01 | H-P SUMP FOR U2 ST2 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C20GMV01XD803XG03 | H-P SUMP FOR U2 ST2 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C20GMV01XD803XG52 | H-P SUMP FOR U2 ST2 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C20GMV01XD803XG54 | H-P SUMP FOR U2 ST2 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6302 | - | LCP | DCDAS | - | - | -
=C00GMV01XD801AXB41 | H-P WW TRANS SUMP Pump A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C00GMV01XD801AXJ51 | H-P WW TRANS SUMP Pump A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C00GMV01XD801BXB41 | H-P WW TRANS SUMP Pump B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C00GMV01XD801BXJ51 | H-P WW TRANS SUMP Pump B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C00GMV01XD801XB40 | H-P WW TRANS SUMP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C00GMV01XD801XG01 | H-P WW TRANS SUMP LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C00GMV01XD801XG03 | H-P WW TRANS SUMP LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C00GMV01XD801XG52 | H-P WW TRANS SUMP LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C00GMV01XD801XG54 | H-P WW TRANS SUMP LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | - | LCP | DCDAS | - | - | -
=C00GMV01BF301XB27 | WW FR U9 & U10 FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 130 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED HEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMV01BF301XQ01 | WW FR U9 & U10 FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 130 | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED HEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMV01BF302XB27 | WW FR LNG TERMINAL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | HOLD | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED HEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMV01BF302XQ01 | WW FR LNG TERMINAL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | HOLD | m3/hr | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED HEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMV01BF303XB27 | FR H-P SUMP SYS TO WWT SYS FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED HEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMV01BF303XQ01 | FR H-P SUMP SYS TO WWT SYS FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (HIGH POLLUTED HEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BF301XB27 | L-P SUMP FOR U1 ST OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 110 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BF301XQ01 | L-P SUMP FOR U1 ST OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 110 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BF302XB27 | L-P SUMP FOR U1 NH3 STG TK OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 145 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BF302XQ01 | L-P SUMP FOR U1 NH3 STG TK OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 145 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01XD801AXB41 | L-P SUMP FOR U1 ST PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD801AXJ51 | L-P SUMP FOR U1 ST PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD801BXB41 | L-P SUMP FOR U1 ST PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD801BXJ51 | L-P SUMP FOR U1 ST PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD801XB40 | L-P SUMP FOR U1 ST LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD801XG01 | L-P SUMP FOR U1 ST LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD801XG03 | L-P SUMP FOR U1 ST LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD801XG52 | L-P SUMP FOR U1 ST LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD801XG54 | L-P SUMP FOR U1 ST LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD802AXB41 | L-P SUMP FOR U1 NH3 STG TK PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD802AXJ51 | L-P SUMP FOR U1 NH3 STG TK PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD802BXB41 | L-P SUMP FOR U1 NH3 STG TK PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD802BXJ51 | L-P SUMP FOR U1 NH3 STG TK PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD802XB40 | L-P SUMP FOR U1 NH3 STG TK LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD802XG01 | L-P SUMP FOR U1 NH3 STG TK LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD802XG03 | L-P SUMP FOR U1 NH3 STG TK LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD802XG52 | L-P SUMP FOR U1 NH3 STG TK LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01XD802XG54 | L-P SUMP FOR U1 NH3 STG TK LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | DWT | TC1-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C10GMW01BF303XQ01 | L-P SUMP FOR U1 OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | HOLD | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | D/P Flow Transmitter | Field | DCDAS | - | - | -
=C10GMW01BF303XQ23 | L-P SUMP FOR U1 OUTL FQIT LOC IND | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | Local Indicator | DCDAS | LCP | - | - | -
=C10GMW01BF304XB27 | L-P SUMP FOR U1 HRSG2 OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 145 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BF304XQ01 | L-P SUMP FOR U1 HRSG2 OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 145 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BL302XQ01 | L-P SUMP FOR U1 HRSG2 LIT | D-AI | 4-20mA | S | 4000 | 3600 | 400 | - | mm | NO | YES | - | - | - | 200 | 6000 | mm | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | Level transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BL303XQ01 | L-P SUMP FOR U1 LIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | HOLD | TC1-1-UWM02-D6202 | HOLD | Field | DCDAS | - | - | -
=C10GMW01XD803AXB41 | L-P SUMP FOR U1 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD803AXJ51 | L-P SUMP FOR U1 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD803BXB41 | L-P SUMP FOR U1 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD803BXJ51 | L-P SUMP FOR U1 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD803XB40 | L-P SUMP FOR U1 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD803XG01 | L-P SUMP FOR U1 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD803XG03 | L-P SUMP FOR U1 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD803XG52 | L-P SUMP FOR U1 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD803XG54 | L-P SUMP FOR U1 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD804AXB41 | L-P SUMP FOR U1 HRSG2 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD804AXJ51 | L-P SUMP FOR U1 HRSG2 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD804BXB41 | L-P SUMP FOR U1 HRSG2 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD804BXJ51 | L-P SUMP FOR U1 HRSG2 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD804XB40 | L-P SUMP FOR U1 HRSG2 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD804XG01 | L-P SUMP FOR U1 HRSG2 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD804XG03 | L-P SUMP FOR U1 HRSG2 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD804XG52 | L-P SUMP FOR U1 HRSG2 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01XD804XG54 | L-P SUMP FOR U1 HRSG2 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMW01BF305XB27 | L-P SUMP FOR U1 HRSG1 BLDN TK OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 11 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BF305XQ01 | L-P SUMP FOR U1 HRSG1 BLDN TK OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 11 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BF306XB27 | L-P SUMP FOR U1 HRSG2 BLDN TK OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 11 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BF306XQ01 | L-P SUMP FOR U1 HRSG2 BLDN TK OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 11 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01XD805AXB41 | L-P SUMP FOR U1 HRSG1 BLDN TK PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD805AXJ51 | L-P SUMP FOR U1 HRSG1 BLDN TK PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD805BXB41 | L-P SUMP FOR U1 HRSG1 BLDN TK PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD805BXJ51 | L-P SUMP FOR U1 HRSG1 BLDN TK PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD805XB40 | L-P SUMP FOR U1 HRSG1 BLDN TK LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD805XG01 | L-P SUMP FOR U1 HRSG1 BLDN TK LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD805XG03 | L-P SUMP FOR U1 HRSG1 BLDN TK LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD805XG52 | L-P SUMP FOR U1 HRSG1 BLDN TK LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD805XG54 | L-P SUMP FOR U1 HRSG1 BLDN TK LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD806AXB41 | L-P SUMP FOR U1 HRSG2 BLDN TK PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD806AXJ51 | L-P SUMP FOR U1 HRSG2 BLDN TK PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD806BXB41 | L-P SUMP FOR U1 HRSG2 BLDN TK PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD806BXJ51 | L-P SUMP FOR U1 HRSG2 BLDN TK PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD806XB40 | L-P SUMP FOR U1 HRSG2 BLDN TK LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD806XG01 | L-P SUMP FOR U1 HRSG2 BLDN TK LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD806XG03 | L-P SUMP FOR U1 HRSG2 BLDN TK LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD806XG52 | L-P SUMP FOR U1 HRSG2 BLDN TK LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01XD806XG54 | L-P SUMP FOR U1 HRSG2 BLDN TK LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C10GMW01BF307XB27 | L-P SUMP FOR U1 ST2 OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01BF307XQ01 | L-P SUMP FOR U1 ST2 OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMW01XD807AXB41 | L-P SUMP FOR U1 ST2 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C10GMW01XD807AXJ51 | L-P SUMP FOR U1 ST2 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C10GMW01XD807BXB41 | L-P SUMP FOR U1 ST2 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C10GMW01XD807BXJ51 | L-P SUMP FOR U1 ST2 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C10GMW01XD807XB40 | L-P SUMP FOR U1 ST2 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C10GMW01XD807XG01 | L-P SUMP FOR U1 ST2 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C10GMW01XD807XG03 | L-P SUMP FOR U1 ST2 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C10GMW01XD807XG52 | L-P SUMP FOR U1 ST2 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C10GMW01XD807XG54 | L-P SUMP FOR U1 ST2 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#1) | ST1 | TC1-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C20GMW01BF301XB27 | L-P SUMP FOR U2 ST OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 110 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF301XQ01 | L-P SUMP FOR U2 ST OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 110 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF302XB27 | L-P SUMP FOR U2 NH3 STG TK OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 145 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF302XQ01 | L-P SUMP FOR U2 NH3 STG TK OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 145 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01XD801AXB41 | L-P SUMP FOR U2 ST PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD801AXJ51 | L-P SUMP FOR U2 ST PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD801BXB41 | L-P SUMP FOR U2 ST PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD801BXJ51 | L-P SUMP FOR U2 ST PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD801XB40 | L-P SUMP FOR U2 ST LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD801XG01 | L-P SUMP FOR U2 ST LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD801XG03 | L-P SUMP FOR U2 ST LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD801XG52 | L-P SUMP FOR U2 ST LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD801XG54 | L-P SUMP FOR U2 ST LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD802AXB41 | L-P SUMP FOR U2 NH3 STG TK PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD802AXJ51 | L-P SUMP FOR U2 NH3 STG TK PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD802BXB41 | L-P SUMP FOR U2 NH3 STG TK PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD802BXJ51 | L-P SUMP FOR U2 NH3 STG TK PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD802XB40 | L-P SUMP FOR U2 NH3 STG TK LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD802XG01 | L-P SUMP FOR U2 NH3 STG TK LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD802XG03 | L-P SUMP FOR U2 NH3 STG TK LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD802XG52 | L-P SUMP FOR U2 NH3 STG TK LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01XD802XG54 | L-P SUMP FOR U2 NH3 STG TK LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | DWT | TC2-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C20GMW01BF303XB27 | L-P SUMP FOR U2 OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | 0 | 2500 | mmH2O | 0 | 935 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF303XQ01 | L-P SUMP FOR U2 OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2500 | mmH2O | 0 | 935 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF303XQ23 | L-P SUMP FOR U2 OUTL FQIT LOC IND | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | Local Indicator | DCDAS | LCP | - | - | -
=C20GMW01BF304XB27 | L-P SUMP FOR U2 HRSG2 OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 145 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF304XQ01 | L-P SUMP FOR U2 HRSG2 OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 145 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BL301XQ01 | L-P SUMP FOR U2 LIT | D-AI | 4-20mA | S | 4000 | 3600 | 400 | - | mm | NO | YES | - | - | - | 200 | 6000 | mm | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | Level transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BL302XQ01 | L-P SUMP FOR U2 HRSG2 LIT | D-AI | 4-20mA | S | 4000 | 3600 | 400 | - | mm | NO | YES | - | - | - | 200 | 6000 | mm | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | Level transmitter | FIELD | DCDAS | - | - | -
=C20GMW01XD803AXB41 | L-P SUMP FOR U2 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD803AXJ51 | L-P SUMP FOR U2 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD803BXB41 | L-P SUMP FOR U2 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD803BXJ51 | L-P SUMP FOR U2 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD803XB40 | L-P SUMP FOR U2 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD803XG01 | L-P SUMP FOR U2 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD803XG03 | L-P SUMP FOR U2 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD803XG52 | L-P SUMP FOR U2 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD803XG54 | L-P SUMP FOR U2 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD804AXB41 | L-P SUMP FOR U2 HRSG2 PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD804AXJ51 | L-P SUMP FOR U2 HRSG2 PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD804BXB41 | L-P SUMP FOR U2 HRSG2 PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD804BXJ51 | L-P SUMP FOR U2 HRSG2 PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD804XB40 | L-P SUMP FOR U2 HRSG2 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD804XG01 | L-P SUMP FOR U2 HRSG2 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD804XG03 | L-P SUMP FOR U2 HRSG2 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD804XG52 | L-P SUMP FOR U2 HRSG2 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01XD804XG54 | L-P SUMP FOR U2 HRSG2 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C20GMW01BF305XB27 | L-P SUMP FOR U2 HRSG1 BLDN TK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 11 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF305XQ01 | L-P SUMP FOR U2 HRSG1 BLDN TK OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 11 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF306XB27 | L-P SUMP FOR U2 HRSG2 BLDN TK FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 11 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF306XQ01 | L-P SUMP FOR U2 HRSG2 BLDN TK OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 11 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01XD805AXB41 | L-P PP A FOR U2 HRSG1 BLDN TK RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD805AXJ51 | L-P PP A FOR U2 HRSG1 BLDN TK OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD805BXB41 | L-P PP B FOR U2 HRSG1 BLDN TK RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD805BXJ51 | L-P PP B FOR U2 HRSG1 BLDN TK OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD805XB40 | L-P SUMP FOR U2 HRSG1 BLDN TK LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD805XG01 | L-P SUMP FOR U2 HRSG1 BLDN TK LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD805XG03 | L-P SUMP FOR U2 HRSG1 BLDN TK LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD805XG52 | L-P SUMP FOR U2 HRSG1 BLDN TK LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD805XG54 | L-P SUMP FOR U2 HRSG1 BLDN TK LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD806AXB41 | L-P PP A FOR U2 HRSG2 BLDN TK RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD806AXJ51 | L-P PP A FOR U2 HRSG2 BLDN TK OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD806BXB41 | L-P PP B FOR U2 HRSG2 BLDN TK RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD806BXJ51 | L-P PP B FOR U2 HRSG2 BLDN TK OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD806XB40 | L-P SUMP FOR U2 HRSG2 BLDN TK LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD806XG01 | L-P SUMP FOR U2 HRSG2 BLDN TK LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD806XG03 | L-P SUMP FOR U2 HRSG2 BLDN TK LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD806XG52 | L-P SUMP FOR U2 HRSG2 BLDN TK LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01XD806XG54 | L-P SUMP FOR U2 HRSG2 BLDN TK LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6203 | - | LCP | DCDAS | - | - | -
=C20GMW01BF307XB27 | L-P SUMP FOR U2 ST2 OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01BF307XQ01 | L-P SUMP FOR U2 ST2 OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMW01XD807AXB41 | L-P PP A FOR U2 ST2 RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C20GMW01XD807AXJ51 | L-P PP A FOR U2 ST2 OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C20GMW01XD807BXB41 | L-P PP B FOR U2 ST2 RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C20GMW01XD807BXJ51 | L-P PP B FOR U2 ST2 OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C20GMW01XD807XB40 | L-P SUMP FOR U2 ST2 LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C20GMW01XD807XG01 | L-P SUMP FOR U2 ST2 LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C20GMW01XD807XG03 | L-P SUMP FOR U2 ST2 LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C20GMW01XD807XG52 | L-P SUMP FOR U2 ST2 LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C20GMW01XD807XG54 | L-P SUMP FOR U2 ST2 LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(CC#2) | ST2 | TC2-1-UWM02-D6204 | - | LCP | DCDAS | - | - | -
=C00GMW01BF306XB27 | FR L-P WW COLL SYS TO WWT SYS FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BF306XQ01 | FR L-P WW COLL SYS TO WWT SYS FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BF307XB27 | UPW TREATMENT WW SUMP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 95 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | ST1 | TC0-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BF307XQ01 | UPW TREATMENT WW SUMP OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 95 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | ST1 | TC0-1-UWM02-D6201 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BL303XQ01 | L-P TRANS SUMP LIT | D-AI | 4-20mA | S | 4000 | 3600 | 400 | - | mm | NO | YES | - | - | - | 200 | 6000 | mm | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | Level transmitter | FIELD | DCDAS | - | - | -
=C00GMW01XD803AXB41 | L-P TRANS SUMP Pump A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C00GMW01XD803AXJ51 | L-P TRANS SUMP Pump A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C00GMW01XD803BXB41 | L-P TRANS SUMP Pump B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C00GMW01XD803BXJ51 | L-P TRANS SUMP Pump B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C00GMW01XD803XB40 | L-P TRANS SUMP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C00GMW01XD803XG01 | L-P TRANS SUMP LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C00GMW01XD803XG03 | L-P TRANS SUMP LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C00GMW01XD803XG52 | L-P TRANS SUMP LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C00GMW01XD803XG54 | L-P TRANS SUMP LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6201 | - | LCP | DCDAS | - | - | -
=C00GMW01BF301XB27 | L-P SUMP FOR DWTS OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | 0 | 2700 | mmH2O | 0 | 340 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BF301XQ01 | L-P SUMP FOR DWTS OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2700 | mmH2O | 0 | 340 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BF301XQ23 | L-P SUMP FOR DWTS OUTL FQIT LOC IND | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | 0 | 340 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | Local Indicator | DCDAS | LCP | - | - | -
=C00GMW01BF302XB27 | L-P SUMP FOR RWTS OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | 0 | 2500 | mmH2O | 0 | 490 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BF302XQ01 | L-P SUMP FOR RWTS OUTL FIT | D-AI | 4-20mA | S | - | - | - | - | - | NO | YES | 0 | 2500 | mmH2O | 0 | 490 | m3/hr | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | D/P Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BF302XQ23 | L-P SUMP FOR RWTS OUTL FQIT LOC IND | D-AO | 4-20mA | S | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | Local Indicator | DCDAS | LCP | - | - | -
=C00GMW01BL301XQ01 | L-P SUMP FOR DWTS LIT | D-AI | 4-20mA | S | 3900 | 3500 | 400 | - | mm | NO | YES | - | - | - | 200 | 5000 | mm | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | Level transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BL302XQ01 | L-P SUMP FOR RWTS LIT | D-AI | 4-20mA | S | 3200 | 2800 | 400 | - | mm | NO | YES | - | - | - | 200 | 5000 | mm | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | Level transmitter | FIELD | DCDAS | - | - | -
=C00GMW01BP301XQ01 | L-P PP FOR DWTS A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GMW01BP302XQ01 | L-P PP FOR DWTS B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GMW01XD801AXB41 | L-P SUMP FOR DWTS PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD801AXJ51 | L-P SUMP FOR DWTS PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD801BXB41 | L-P SUMP FOR DWTS PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD801BXJ51 | L-P SUMP FOR DWTS PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD801XB40 | L-P SUMP FOR DWTS LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD801XG01 | L-P SUMP FOR DWTS LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD801XG03 | L-P SUMP FOR DWTS LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD801XG52 | L-P SUMP FOR DWTS LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD801XG54 | L-P SUMP FOR DWTS LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | WWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD802AXB41 | L-P SUMP FOR RWTS PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD802AXJ51 | L-P SUMP FOR RWTS PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD802BXB41 | L-P SUMP FOR RWTS PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD802BXJ51 | L-P SUMP FOR RWTS PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD802XB40 | L-P SUMP FOR RWTS LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD802XG01 | L-P SUMP FOR RWTS LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD802XG03 | L-P SUMP FOR RWTS LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD802XG52 | L-P SUMP FOR RWTS LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C00GMW01XD802XG54 | L-P SUMP FOR RWTS LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (LOW POLLUTED CHEMICAL)(COMMON) | DWT | TC0-1-UWM02-D6202 | - | LCP | DCDAS | - | - | -
=C10GMX01BF301XB27 | OILY SUMP FOR U1 ST OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMX01BF301XQ01 | OILY SUMP FOR U1 ST OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMX01BF302XB27 | OILY SUMP FOR U1 GT/HRSG OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMX01BF302XQ01 | OILY SUMP FOR U1 GT/HRSG OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMX01BL011XG01 | CATCH BSN FOR U1 ST XFMR LSH | D-DI | 24VDC | S | - | 800 | - | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C10GMX01BL011XG52 | CATCH BSN FOR U1 ST XFMR LSL | D-DI | 24VDC | S | - | - | 600 | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C10GMX01BL012XG01 | CATCH BSN FOR U1 GT1 XFMR LSH | D-DI | 24VDC | S | - | 800 | - | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C10GMX01BL012XG52 | CATCH BSN FOR U1 GT1 XFMR LSL | D-DI | 24VDC | S | - | - | 600 | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C10GMX01BL013XG01 | CATCH BSN FOR U1 GT2 XFMR LSH | D-DI | 24VDC | S | - | 800 | - | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C10GMX01BL013XG52 | CATCH BSN FOR U1 GT1 XFMR LSL | D-DI | 24VDC | S | - | - | 600 | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C10GMX01BL301XQ01 | OILY SUMP FOR U1 ST LIT | D-AI | 4-20mA | S | 2300 | 2100 | 200 | - | mm | NO | YES | - | - | - | 200 | 4000 | mm | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | Level transmitter | FIELD | DCDAS | - | - | -
=C10GMX01BL302XQ01 | OILY SUMP FOR GT/HRSG LIT | D-AI | 4-20mA | S | 2200 | 2000 | 200 | - | mm | NO | YES | - | - | - | 200 | 5000 | mm | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | Level transmitter | FIELD | DCDAS | - | - | -
=C10GMX01HQ001XB01 | OILY SEPR FOR U1 ST RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01HQ001XB48 | OILY SEPR FOR U1 ST FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01HQ002XB01 | OILY SEPR FOR U1 GT/HRSG RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01HQ002XB48 | OILY SEPR FOR U1 GT/HRSG FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01QM461XB62 | CATCH BSN FOR U1 ST XFMR TO OILY SUMP XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | On Off Valve (Gate Valve) | DCDAS | Field | - | - | -
=C10GMX01QM461XG01 | CATCH BSN FOR U1 ST XFMR TO OILY SUMP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C10GMX01QM461XG02 | CATCH BSN FOR U1 ST XFMR TO OILY SUMP XV-CLS CMD | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C10GMX01QM462XB62 | CATCH BSN FOR U1 GT1 XFMR TO OILY SUMP XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | On Off Valve (Gate Valve) | DCDAS | Field | - | - | -
=C10GMX01QM462XG01 | CATCH BSN FOR U1 GT1 XFMR TO OILY SUMP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C10GMX01QM462XG02 | CATCH BSN FOR U1 GT1 XFMR TO OILY SUMP XV-CLS CMD | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C10GMX01QM463XB62 | CATCH BSN FOR U1 GT2 XFMR TO OILY SUMP XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | On Off Valve (Gate Valve) | DCDAS | Field | - | - | -
=C10GMX01QM463XG01 | CATCH BSN FOR U1 GT2 XFMR TO OILY SUMP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C10GMX01QM463XG02 | CATCH BSN FOR U1 GT2 XFMR TO OILY SUMP XV-CLS CMD | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | HOLD | TC1-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C10GMX01XD801AXB41 | OILY SUMP FOR U1 ST PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD801AXJ51 | OILY SUMP FOR U1 ST PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD801BXB41 | OILY SUMP FOR U1 ST PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD801BXJ51 | OILY SUMP FOR U1 ST PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD801XB40 | OILY SUMP FOR U1 ST LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD801XG01 | OILY SUMP FOR U1 ST LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD801XG03 | OILY SUMP FOR U1 ST LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD801XG52 | OILY SUMP FOR U1 ST LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD801XG54 | OILY SUMP FOR U1 ST LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD802AXB41 | OILY SUMP FOR U1 GT/HRSG PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD802AXJ51 | OILY SUMP FOR U1 GT/HRSG PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD802BXB41 | OILY SUMP FOR U1 GT/HRSG PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD802BXJ51 | OILY SUMP FOR U1 GT/HRSG PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD802XB40 | OILY SUMP FOR U1 GT/HRSG LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD802XG01 | OILY SUMP FOR U1 GT/HRSG LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD802XG03 | OILY SUMP FOR U1 GT/HRSG LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD802XG52 | OILY SUMP FOR U1 GT/HRSG LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C10GMX01XD802XG54 | OILY SUMP FOR U1 GT/HRSG LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#1) | GT1 | TC1-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01BF301XB27 | OILY SUMP FOR U2 ST OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMX01BF301XQ01 | OILY SUMP FOR U2 ST OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMX01BF302XB27 | OILY SUMP FOR U2 GT/HRSG OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMX01BF302XQ01 | OILY SUMP FOR U2 GT/HRSG OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMX01BL011XG01 | CATCH BSN FOR U2 ST XFMR LSH | D-DI | 24VDC | S | - | 800 | - | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C20GMX01BL011XG52 | CATCH BSN FOR U2 ST XFMR LSL | D-DI | 24VDC | S | - | - | 600 | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C20GMX01BL012XG01 | CATCH BSN FOR U2 GT1 XFMR LSH | D-DI | 24VDC | S | - | 800 | - | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C20GMX01BL012XG52 | CATCH BSN FOR U2 GT1 XFMR LSL | D-DI | 24VDC | S | - | - | 600 | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C20GMX01BL013XG01 | CATCH BSN FOR U2 GT2 XFMR LSH | D-DI | 24VDC | S | - | 800 | - | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C20GMX01BL013XG52 | CATCH BSN FOR U2 GT1 XFMR LSL | D-DI | 24VDC | S | - | - | 600 | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | Float Level Switch | Field | DCDAS | - | - | -
=C20GMX01BL301XQ01 | OILY SUMP FOR U2 ST LIT | D-AI | 4-20mA | S | 2300 | 2100 | 200 | - | mm | NO | YES | - | - | - | 200 | 4000 | mm | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | Level transmitter | FIELD | DCDAS | - | - | -
=C20GMX01BL302XQ01 | OILY SUMP FOR U2 GT/HRSG LIT | D-AI | 4-20mA | S | 2200 | 2000 | 200 | - | mm | NO | YES | - | - | - | 200 | 5000 | mm | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | Level transmitter | FIELD | DCDAS | - | - | -
=C20GMX01HQ001XB01 | OILY SEPR FOR U2 ST RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01HQ001XB48 | OILY SEPR FOR U2 ST FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01HQ002XB01 | OILY SEPR FOR U2 GT/HRSG RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01HQ002XB48 | OILY SEPR FOR U2 GT/HRSG FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01QM461XB62 | CATCH BSN FOR U2 ST XFMR TO OILY SUMP XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | DCDAS | Field | - | - | -
=C20GMX01QM461XG01 | CATCH BSN FOR U2 ST XFMR TO OILY SUMP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C20GMX01QM461XG02 | CATCH BSN FOR U2 ST XFMR TO OILY SUMP XV-CLS CMD | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C20GMX01QM462XB62 | CATCH BSN FOR U2 GT1 XFMR TO OILY SUMP XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | DCDAS | Field | - | - | -
=C20GMX01QM462XG01 | CATCH BSN FOR U2 GT1 XFMR TO OILY SUMP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C20GMX01QM462XG02 | CATCH BSN FOR U2 GT1 XFMR TO OILY SUMP XV-CLS CMD | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C20GMX01QM463XB62 | CATCH BSN FOR U2 GT2 XFMR TO OILY SUMP XV-CLS CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | DCDAS | Field | - | - | -
=C20GMX01QM463XG01 | CATCH BSN FOR U2 GT2 XFMR TO OILY SUMP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C20GMX01QM463XG02 | CATCH BSN FOR U2 GT2 XFMR TO OILY SUMP XV-CLS CMD | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C20GMX01XD801AXB41 | OILY SUMP FOR U2 ST PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD801AXJ51 | OILY SUMP FOR U2 ST PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD801BXB41 | OILY SUMP FOR U2 ST PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD801BXJ51 | OILY SUMP FOR U2 ST PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD801XB40 | OILY SUMP FOR U2 ST LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD801XG01 | OILY SUMP FOR U2 ST LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD801XG03 | OILY SUMP FOR U2 ST LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD801XG52 | OILY SUMP FOR U2 ST LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD801XG54 | OILY SUMP FOR U2 ST LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD802AXB41 | OILY SUMP FOR U2 GT/HRSG PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD802AXJ51 | OILY SUMP FOR U2 GT/HRSG PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD802BXB41 | OILY SUMP FOR U2 GT/HRSG PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD802BXJ51 | OILY SUMP FOR U2 GT/HRSG PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD802XB40 | OILY SUMP FOR U2 GT/HRSG LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD802XG01 | OILY SUMP FOR U2 GT/HRSG LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD802XG03 | OILY SUMP FOR U2 GT/HRSG LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD802XG52 | OILY SUMP FOR U2 GT/HRSG LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20GMX01XD802XG54 | OILY SUMP FOR U2 GT/HRSG LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | GT2 | TC2-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C20QEA01QM061XB61 | PA HDR TO STORM DITCH XV-OPEN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | DCDAS | Field | - | - | -
=C20QEA01QM061XG01 | PA HDR TO STORM DITCH XV-OPEN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C20QEA01QM061XG02 | PA HDR TO STORM DITCH XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(CC#2) | HOLD | TC2-1-UWM02-D6101 | On Off Valve (Gate Valve) | Field | DCDAS | - | - | -
=C00GMX01BF305XB27 | FR PWR BLK 1.5M OUTS TO WW TREAT SYS FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | HOLD | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF305XQ01 | FR PWR BLK 1.5M OUTS TO WW TREAT SYS FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | HOLD | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF306XB27 | FR OILY WW COLL SYS TO WW TREAT SYS FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF306XQ01 | FR OILY WW COLL SYS TO WW TREAT SYS FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF307XB27 | OILY WW FR ADMIN BLD FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 45 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | MCB | TC0-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF307XQ01 | OILY WW FR ADMIN BLD FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 45 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | MCB | TC0-1-UWM02-D6101 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF308XQ01 | OILY WW TRANS SUMP OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | HOLD | TC0-1-UWM02-D6101 | Magnetic Flow Transmitter | Field | DCDAS | - | - | -
=C00GMX01HQ004XB01 | OILY SEPR PP FOR GT MAINT RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01HQ004XB48 | OILY SEPR PP FOR GT MAINT FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01XD804AXB41 | OILY SUMP FOR GT MAINT PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01XD804AXJ51 | OILY SUMP FOR GT MAINT PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01XD804BXB41 | OILY SUMP FOR GT MAINT PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01XD804BXJ51 | OILY SUMP FOR GT MAINT PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01XD804XB40 | OILY SUMP FOR GT MAINT LCP LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01XD804XG01 | OILY SUMP FOR GT MAINT LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01XD804XG03 | OILY SUMP FOR GT MAINT LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01XD804XG52 | OILY SUMP FOR GT MAINT LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01XD804XG54 | OILY SUMP FOR GT MAINT LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | WWT | TC0-1-UWM02-D6101 | - | LCP | DCDAS | - | - | -
=C00GMX01BF302XB27 | OIL SUMP FOR FIRE WTR PP OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 27 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF302XQ01 | OIL SUMP FOR FIRE WTR PP OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 27 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01HQ002XB01 | OILY SEPR FOR FIRE WTR PP HSE RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01HQ002XB48 | OILY SEPR FOR FIRE WTR PP HSE FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01XD802AXB41 | OIL SUMP FOR FIRE WTR PP PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01XD802AXJ51 | OIL SUMP FOR FIRE WTR PP PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01XD802BXB41 | OIL SUMP FOR FIRE WTR PP PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01XD802BXJ51 | OIL SUMP FOR FIRE WTR PP PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01XD802XB40 | OIL SUMP FOR FIRE WTR PP LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01XD802XG01 | OIL SUMP FOR FIRE WTR PP LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01XD802XG03 | OIL SUMP FOR FIRE WTR PP LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01XD802XG52 | OIL SUMP FOR FIRE WTR PP LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01XD802XG54 | OIL SUMP FOR FIRE WTR PP LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | RFW | TC0-1-UWM02-D6102 | - | LCP | DCDAS | - | - | -
=C00GMX01BF301XB27 | OILY SUMP FOR NGS OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 27 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF301XQ01 | OILY SUMP FOR NGS OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 27 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF303XB27 | OILY SUMP FOR GT MAINT OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01BF303XQ01 | OILY SUMP FOR GT MAINT OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 35 | m3/hr | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMX01HQ001XB01 | OILY SEPR FOR NGS RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01HQ001XB48 | OILY SEPR FOR NGS FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01HQ003XB01 | OILY SEPR FOR TRANS SUMP PP RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01HQ003XB48 | OILY SEPR FOR TRANS SUMP PP FAULT | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD801AXB41 | OILY SUMP FOR NGS PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD801AXJ51 | OILY SUMP FOR NGS PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD801BXB41 | OILY SUMP FOR NGS PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD801BXJ51 | OILY SUMP FOR NGS PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD801XB40 | OILY SUMP FOR NGS LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD801XG01 | OILY SUMP FOR NGS LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD801XG03 | OILY SUMP FOR NGS LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD801XG52 | OILY SUMP FOR NGS LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD801XG54 | OILY SUMP FOR NGS LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | NGS | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD803AXB41 | OILY WW TRANS SUMP PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD803AXJ51 | OILY WW TRANS SUMP PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD803BXB41 | OILY WW TRANS SUMP PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD803BXJ51 | OILY WW TRANS SUMP PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD803XB40 | OILY WW TRANS SUMP LCP LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD803XG01 | OILY WW TRANS SUMP LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD803XG03 | OILY WW TRANS SUMP LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD803XG52 | OILY WW TRANS SUMP LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMX01XD803XG54 | OILY WW TRANS SUMP LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (OILY)(COMMON) | DWT | TC0-1-UWM02-D6103 | - | LCP | DCDAS | - | - | -
=C00GMB01BF301XB27 | TO EX SANIT WWT FACIL FQIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMB01BF301XQ01 | TO EX SANIT WWT FACIL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GMB01BF302XQ01 | SWES & CWP HSE TO U9 & U10 SWES HSE SANIT WW FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6401 | Magnetic Flow Transmitter | Field | DCDAS | - | - | -
=C00GMB01XD805AXB41 | SANIT SUMP FOR HVY PT WHSE PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | - | LCP | DCDAS | - | - | -
=C00GMB01XD805AXJ51 | SANIT SUMP FOR HVY PT WHSE PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | - | LCP | DCDAS | - | - | -
=C00GMB01XD805BXB41 | SANIT SUMP FOR HVY PT WHSE PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | - | LCP | DCDAS | - | - | -
=C00GMB01XD805BXJ51 | SANIT SUMP FOR HVY PT WHSE PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | - | LCP | DCDAS | - | - | -
=C00GMB01XD805XB40 | SANIT SUMP FOR HVY PT WHSE LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | - | LCP | DCDAS | - | - | -
=C00GMB01XD805XG01 | SANIT SUMP FOR HVY PT WHSE LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | - | LCP | DCDAS | - | - | -
=C00GMB01XD805XG03 | SANIT SUMP FOR HVY PT WHSE LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | - | LCP | DCDAS | - | - | -
=C00GMB01XD805XG52 | SANIT SUMP FOR HVY PT WHSE LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | - | LCP | DCDAS | - | - | -
=C00GMB01XD805XG54 | SANIT SUMP FOR HVY PT WHSE LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | MCB | TC0-1-UWM02-D6401 | - | LCP | DCDAS | - | - | -
=C00GMB01XD801AXB41 | SANIT SUMP FOR SWES & CWP PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | SWE | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C00GMB01XD801AXJ51 | SANIT SUMP FOR SWES & CWP PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | SWE | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C00GMB01XD801BXB41 | SANIT SUMP FOR SWES & CWP PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | SWE | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C00GMB01XD801BXJ51 | SANIT SUMP FOR SWES & CWP PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | SWE | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C00GMB01XD801XB40 | SANIT SUMP FOR SWES & CWP LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | SWE | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C00GMB01XD801XG01 | SANIT SUMP FOR SWES & CWP LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | SWE | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C00GMB01XD801XG03 | SANIT SUMP FOR SWES & CWP LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | SWE | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C00GMB01XD801XG52 | SANIT SUMP FOR SWES & CWP LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | SWE | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C00GMB01XD801XG54 | SANIT SUMP FOR SWES & CWP LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | SWE | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD801AXB41 | SANIT SUMP FOR U1 ST ELEC BLD PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD801AXJ51 | SANIT SUMP FOR U1 ST ELEC BLD PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD801BXB41 | SANIT SUMP FOR U1 ST ELEC BLD PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD801BXJ51 | SANIT SUMP FOR U1 ST ELEC BLD PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD801XB40 | SANIT SUMP FOR U1 ST ELEC BLD LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD801XG01 | SANIT SUMP FOR U1 ST ELEC BLD LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD801XG03 | SANIT SUMP FOR U1 ST ELEC BLD LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD801XG52 | SANIT SUMP FOR U1 ST ELEC BLD LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD801XG54 | SANIT SUMP FOR U1 ST ELEC BLD LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD802AXB41 | SANIT SUMP FOR U1 GT ELEC BLD PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD802AXJ51 | SANIT SUMP FOR U1 GT ELEC BLD PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD802BXB41 | SANIT SUMP FOR U1 GT ELEC BLD PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD802BXJ51 | SANIT SUMP FOR U1 GT ELEC BLD PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD802XB40 | SANIT SUMP FOR U1 GT ELEC BLD LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD802XG01 | SANIT SUMP FOR U1 GT ELEC BLD LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD802XG03 | SANIT SUMP FOR U1 GT ELEC BLD LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD802XG52 | SANIT SUMP FOR U1 GT ELEC BLD LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C10GMB01XD802XG54 | SANIT SUMP FOR U1 GT ELEC BLD LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT1 | TC0-1-UWM02-D6402 | - | LCP | DCDAS | - | - | -
=C00GMB01XD803AXB41 | SANIT SUMP FOR NGS PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | NGS | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD803AXJ51 | SANIT SUMP FOR NGS PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | NGS | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD803BXB41 | SANIT SUMP FOR NGS PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | NGS | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD803BXJ51 | SANIT SUMP FOR NGS PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | NGS | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD803XB40 | SANIT SUMP FOR NGS LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | NGS | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD803XG01 | SANIT SUMP FOR NGS LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | NGS | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD803XG03 | SANIT SUMP FOR NGS LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | NGS | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD803XG52 | SANIT SUMP FOR NGS LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | NGS | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD803XG54 | SANIT SUMP FOR NGS LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | NGS | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD806AXB41 | SANIT WW TRANS SUMP PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD806AXJ51 | SANIT WW TRANS SUMP PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD806BXB41 | SANIT WW TRANS SUMP PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD806BXJ51 | SANIT WW TRANS SUMP PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD806XB40 | SANIT WW TRANS SUMP LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD806XG01 | SANIT WW TRANS SUMP LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD806XG03 | SANIT WW TRANS SUMP LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD806XG52 | SANIT WW TRANS SUMP LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD806XG54 | SANIT WW TRANS SUMP LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6403 | - | LCP | DCDAS | - | - | -
=C00GMB01XD804AXB41 | SANIT SUMP FOR DWTS BLD PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | DWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD804AXJ51 | SANIT SUMP FOR DWTS BLD PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | DWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD804BXB41 | SANIT SUMP FOR DWTS BLD PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | DWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD804BXJ51 | SANIT SUMP FOR DWTS BLD PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | DWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD804XB40 | SANIT SUMP FOR DWTS BLD LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | DWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD804XG01 | SANIT SUMP FOR DWTS BLD LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | DWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD804XG03 | SANIT SUMP FOR DWTS BLD LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | DWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD804XG52 | SANIT SUMP FOR DWTS BLD LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | DWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD804XG54 | SANIT SUMP FOR DWTS BLD LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | DWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD807AXB41 | SANIT SUMP FOR AWWTS & WWTS BLD PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD807AXJ51 | SANIT SUMP FOR AWWTS & WWTS BLD PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD807BXB41 | SANIT SUMP FOR AWWTS & WWTS BLD PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD807BXJ51 | SANIT SUMP FOR AWWTS & WWTS BLD PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD807XB40 | SANIT SUMP FOR AWWTS & WWTS BLD LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD807XG01 | SANIT SUMP FOR AWWTS & WWTS BLD LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD807XG03 | SANIT SUMP FOR AWWTS & WWTS BLD LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD807XG52 | SANIT SUMP FOR AWWTS & WWTS BLD LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD807XG54 | SANIT SUMP FOR AWWTS & WWTS BLD LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6404 | - | LCP | DCDAS | - | - | -
=C00GMB01XD802AXB41 | SANIT SUMP FOR GT MAINT PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C00GMB01XD802AXJ51 | SANIT SUMP FOR GT MAINT PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C00GMB01XD802BXB41 | SANIT SUMP FOR GT MAINT PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C00GMB01XD802BXJ51 | SANIT SUMP FOR GT MAINT PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C00GMB01XD802XB40 | SANIT SUMP FOR GT MAINT LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C00GMB01XD802XG01 | SANIT SUMP FOR GT MAINT LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C00GMB01XD802XG03 | SANIT SUMP FOR GT MAINT LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C00GMB01XD802XG52 | SANIT SUMP FOR GT MAINT LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C00GMB01XD802XG54 | SANIT SUMP FOR GT MAINT LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | WWT | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD801AXB41 | SANIT SUMP FOR U2 ST BLD PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD801AXJ51 | SANIT SUMP FOR U2 ST BLD PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD801BXB41 | SANIT SUMP FOR U2 ST BLD PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD801BXJ51 | SANIT SUMP FOR U2 ST BLD PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD801XB40 | SANIT SUMP FOR U2 ST BLD LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD801XG01 | SANIT SUMP FOR U2 ST BLD LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD801XG03 | SANIT SUMP FOR U2 ST BLD LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD801XG52 | SANIT SUMP FOR U2 ST BLD LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD801XG54 | SANIT SUMP FOR U2 ST BLD LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | ST2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD802AXB41 | SANIT SUMP FOR U2 GT BLD PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD802AXJ51 | SANIT SUMP FOR U2 GT BLD PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD802BXB41 | SANIT SUMP FOR U2 GT BLD PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD802BXJ51 | SANIT SUMP FOR U2 GT BLD PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD802XB40 | SANIT SUMP FOR U2 GT BLD LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD802XG01 | SANIT SUMP FOR U2 GT BLD LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD802XG03 | SANIT SUMP FOR U2 GT BLD LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD802XG52 | SANIT SUMP FOR U2 GT BLD LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C20GMB01XD802XG54 | SANIT SUMP FOR U2 GT BLD LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SANITARY)(COMMON) | GT2 | TC0-1-UWM02-D6405 | - | LCP | DCDAS | - | - | -
=C10GMY01BF301XB27 | SW LKG SUMP FOR U1 ST OUTL OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMY01BF301XQ01 | SW LKG SUMP FOR U1 ST OUTL OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMY01BF302XB27 | SW LKG SUMP FOR U1 ST INL OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMY01BF302XQ01 | SW LKG SUMP FOR U1 ST INL OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C10GMY01XD801AXB41 | SW LKG SUMP FOR U1 ST INL PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD801AXJ51 | SW LKG SUMP FOR U1 ST INL PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD801BXB41 | SW LKG SUMP FOR U1 ST INL PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD801BXJ51 | SW LKG SUMP FOR U1 ST INL PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD801XB40 | SW LKG SUMP FOR U1 ST INL LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD801XG01 | SW LKG SUMP FOR U1 ST INL LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD801XG03 | SW LKG SUMP FOR U1 ST INL LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD801XG52 | SW LKG SUMP FOR U1 ST INL LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD801XG54 | SW LKG SUMP FOR U1 ST INL LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD802AXB41 | SW LKG SUMP FOR U1 ST OUTL PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD802AXJ51 | SW LKG SUMP FOR U1 ST OUTL PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD802BXB41 | SW LKG SUMP FOR U1 ST OUTL PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD802BXJ51 | SW LKG SUMP FOR U1 ST OUTL PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD802XB40 | SW LKG SUMP FOR U1 ST OUTL LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD802XG01 | SW LKG SUMP FOR U1 ST OUTL LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD802XG03 | SW LKG SUMP FOR U1 ST OUTL LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD802XG52 | SW LKG SUMP FOR U1 ST OUTL LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C10GMY01XD802XG54 | SW LKG SUMP FOR U1 ST OUTL LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#1) | ST1 | TC1-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01BF301XB27 | SW LKG SUMP FOR U2 ST OUTL OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMY01BF301XQ01 | SW LKG SUMP FOR U2 ST OUTL OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMY01BF302XB27 | SW LKG SUMP FOR U2 ST INL OUTL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMY01BF302XQ01 | SW LKG SUMP FOR U2 ST INL OUTL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | 0 | 70 | m3/hr | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C20GMY01XD801AXB41 | SW LKG SUMP FOR U2 ST INL PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD801AXJ51 | SW LKG SUMP FOR U2 ST INL PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD801BXB41 | SW LKG SUMP FOR U2 ST INL PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD801XB40 | SW LKG SUMP FOR U2 ST INL LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD801XG01 | SW LKG SUMP FOR U2 ST INL LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD801XG03 | SW LKG SUMP FOR U2 ST INL LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD801XG52 | SW LKG SUMP FOR U2 ST INL LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD801XG54 | SW LKG SUMP FOR U2 ST INL LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD801XJ51 | SW LKG SUMP FOR U2 ST INL PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD802AXB41 | SW LKG SUMP FOR U2 ST OUTL PP A RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD802AXJ51 | SW LKG SUMP FOR U2 ST OUTL PP A OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD802BXB41 | SW LKG SUMP FOR U2 ST OUTL PP B RUN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD802XB40 | SW LKG SUMP FOR U2 ST OUTL LCP CMN ALM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD802XG01 | SW LKG SUMP FOR U2 ST OUTL LSH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD802XG03 | SW LKG SUMP FOR U2 ST OUTL LSHH | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD802XG52 | SW LKG SUMP FOR U2 ST OUTL LSL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD802XG54 | SW LKG SUMP FOR U2 ST OUTL LSLL | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C20GMY01XD802XJ51 | SW LKG SUMP FOR U2 ST OUTL PP B OL | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER COLLECTION SYSTEM (SEAWATER LEAKAGE) (CC#2) | ST2 | TC2-1-UWM02-D6501 | - | LCP | DCDAS | - | - | -
=C00GAF01QM162XB61 | MISC WTR FEED PP TO CHEM EPA SPL PIT XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | On off Valve (Gate Valve) | DCDAS | FIELD | - | - | -
=C00GAF01QM162XG01 | MISC WTR FEED PP TO CHEM EPA SPL PIT XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GAF01QM162XG02 | MISC WTR FEED PP TO CHEM EPA SPL PIT XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | On off Valve (Gate Valve) | FIELD | DCDAS | - | - | -
=C00GNA01BF301XB27 | EPA SAMPLING PIT FOR CHE INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | NGS | TC0-1-KWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNA01BF301XQ01 | EPA SAMPLING PIT FOR CHE INL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | NGS | TC0-1-KWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNZ01BF301XB27 | MISC WTR POINT OF USE FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNZ01BF301XQ01 | MISC WTR POINT OF USE FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNZ01BF302XB27 | RAINWTR STG TK INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNZ01BF302XQ01 | RAINWTR STG TK INL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNZ01BF303XB27 | MISC WTR TK INL FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNZ01BF303XQ01 | MISC WTR TK INL FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNZ01BL001XG01 | MISC WTR TK LSH | D-DI | 24VDC | S | - | 2100 | - | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GNZ01BL001XG03 | MISC WTR TK LSHH | D-DI | 24VDC | S | 2350 | - | - | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GNZ01BL001XG52 | MISC WTR TK LSL | D-DI | 24VDC | S | - | - | 250 | - | mm | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GNZ01BL001XG54 | MISC WTR TK LSLL | D-DI | 24VDC | S | - | - | - | 0 | mm | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Float Level Switch | FIELD | DCDAS | - | - | -
=C00GNZ01BL301XQ01 | MISC WTR TK LIT | D-AI | 4-20mA | S | 2350 | 2100 | 250 | - | mm | NO | YES | - | - | - | 200 | 2500 | mm | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | Level transmitter | FIELD | DCDAS | - | - | -
=C00GNZ01BP301XQ01 | RAW WTR TRANS PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | DWT | TC0-1-KWM02-D6301 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GNZ01BP302XQ01 | RAW WTR TRANS PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | DWT | TC0-1-KWM02-D6301 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GNZ01BP303XQ01 | RAW WTR TRANS PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.445 | - | MPaG | NO | YES | - | - | - | 0 | 0.936 | MPaG | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | DWT | TC0-1-KWM02-D6301 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GNZ01GP501XB01 | MISC WTR PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | MCC | DCDAS | - | - | -
=C00GNZ01GP501XB49 | MISC WTR PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | MCC | DCDAS | - | - | -
=C00GNZ01GP501XB50 | MISC WTR PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | MCC | DCDAS | - | - | -
=C00GNZ01GP501XB61 | MISC WTR PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | DCDAS | MCC | - | - | -
=C00GNZ01GP501XB62 | MISC WTR PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | DCDAS | MCC | - | - | -
=C00GNZ01GP501XB69 | MISC WTR PP A STOP CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | DCDAS | MCC | - | - | -
=C00GNZ01GP501XB78 | MISC WTR PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | MCC | DCDAS | - | - | -
=C00GNZ01GP511XB01 | MISC WTR PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | MCC | DCDAS | - | - | -
=C00GNZ01GP511XB49 | MISC WTR PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | MCC | DCDAS | - | - | -
=C00GNZ01GP511XB50 | MISC WTR PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | MCC | DCDAS | - | - | -
=C00GNZ01GP511XB61 | MISC WTR PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | DCDAS | MCC | - | - | -
=C00GNZ01GP511XB62 | MISC WTR PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | DCDAS | MCC | - | - | -
=C00GNZ01GP511XB69 | MISC WTR PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | DCDAS | MCC | - | - | -
=C00GNZ01GP511XB78 | MISC WTR PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | - | MCC | DCDAS | - | - | -
=C00GNZ01QM162XB61 | FR REUSE WTR TREAT SYS XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | On off Valve (Butterfly) | DCDAS | FIELD | - | - | -
=C00GNZ01QM162XG01 | FR REUSE WTR TREAT SYS XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GNZ01QM162XG02 | FR REUSE WTR TREAT SYS XV-CLS | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | MCB | TC0-1-KWM02-D6301 | On off Valve (Butterfly) | FIELD | DCDAS | - | - | -
=C00GDA01QM161XB61 | FR RO TREAT WTR PP XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve - Solenoid Valve Open Command | DCDAS | Field | - | - | -
=C00GDA01QM161XG01 | FR RO TREAT WTR PP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve - Valve Open | Field | DCDAS | - | - | -
=C00GDA01QM161XG02 | FR RO TREAT WTR PP XV-CLOSE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve - Valve Close | Field | DCDAS | - | - | -
=C00GNA01QM161XB61 | TO EX TREAT WW STG TK OF U9 & U10 XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve (Butterfly) | DCDAS | Field | - | - | -
=C00GNA01QM161XG01 | TO EX TREAT WW STG TK OF U9 & U10 XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve (Butterfly) | Field | DCDAS | - | - | -
=C00GNA01QM161XG02 | TO EX TREAT WW STG TK OF U9 & U10 XV-CLOSE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve (Butterfly) | Field | DCDAS | - | - | -
=C00GNA01QM162XB61 | TO FGD XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve (Butterfly) | DCDAS | Field | - | - | -
=C00GNA01QM162XG01 | TO FGD XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve (Butterfly) | Field | DCDAS | - | - | -
=C00GNA01QM162XG02 | TO FGD XV-CLOSE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve (Butterfly) | Field | DCDAS | - | - | -
=C00GNA01QM163XB61 | FR #1 TREAT WTR PP XV-OPN CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve (Butterfly) | DCDAS | Field | - | - | -
=C00GNA01QM163XG01 | FR #1 TREAT WTR PP XV-OPN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve (Butterfly) | Field | DCDAS | - | - | -
=C00GNA01QM163XG02 | FR #1 TREAT WTR PP XV-CLOSE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | On Off Valve (Butterfly) | Field | DCDAS | - | - | -
=C00GNA70BF303XQ01 | FR #1 & RO TREAT WTR PP FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | By Vendor | By Vendor | m3/hr | By Vendor | By Vendor | m3/hr | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | HOLD | TC0-1-KWM02-D6302 | Magnetic Flow Transmitter | Field | DCDAS | - | - | -
=C00GNU01BF301XB27 | FR #2 TREATED WTR PP FQIT | D-PL | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNU01BF301XQ01 | FR #2 TREATED WTR PP FIT | D-AI | 4-20mA | F | - | - | - | - | - | NO | YES | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | Magnetic Flow Transmitter | FIELD | DCDAS | - | - | -
=C00GNU01BP301XQ01 | #2 TREATED WTR PP A INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GNU01BP302XQ01 | #2 TREATED WTR PP B INL STR PDIT | D-AI | 4-20mA | S | - | 0.01 | - | - | MPa | NO | YES | 0 | 0.012 | MPa | 0 | 0.012 | MPa | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | D/P Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GNU01BP303XQ01 | TO #2 TREATED WTR PPS PIT | D-AI | 4-20mA | S | - | - | - | 0 | MPaG | NO | YES | - | - | - | 0 | 0.144 | MPaG | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GNU01BP304XQ01 | #2 TREATED WTR PP OUTL PIT | D-AI | 4-20mA | S | - | - | 0.414 | - | MPaG | NO | YES | - | - | - | 0 | 0.872 | MPaG | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | Pressure Transmitter Diaphragm Type | FIELD | DCDAS | - | - | -
=C00GNU01GP501XB01 | #2 TREATED WTR PP A ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | MCC | DCDAS | - | - | -
=C00GNU01GP501XB49 | #2 TREATED WTR PP A ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | MCC | DCDAS | - | - | -
=C00GNU01GP501XB50 | #2 TREATED WTR PP A PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | MCC | DCDAS | - | - | -
=C00GNU01GP501XB61 | #2 TREATED WTR PP A ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | DCDAS | MCC | - | - | -
=C00GNU01GP501XB62 | #2 TREATED WTR PP A OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | DCDAS | MCC | - | - | -
=C00GNU01GP501XB69 | #2 TREATED WTR PP A STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | DCDAS | MCC | - | - | -
=C00GNU01GP501XB78 | #2 TREATED WTR PP A REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | MCC | DCDAS | - | - | -
=C00GNU01GP511XB01 | #2 TREATED WTR PP B ON RETURN | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | MCC | DCDAS | - | - | -
=C00GNU01GP511XB49 | #2 TREATED WTR PP B ELEC TRIP | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | MCC | DCDAS | - | - | -
=C00GNU01GP511XB50 | #2 TREATED WTR PP B PWR NORM | D-DI | 24VDC | S | - | - | - | - | - | NO | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | MCC | DCDAS | - | - | -
=C00GNU01GP511XB61 | #2 TREATED WTR PP B ON CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | DCDAS | MCC | - | - | -
=C00GNU01GP511XB62 | #2 TREATED WTR PP B OFF CMD | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | DCDAS | MCC | - | - | -
=C00GNU01GP511XB69 | #2 TREATED WTR PP B STOP | D-DO | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | DCDAS | MCC | - | - | -
=C00GNU01GP511XB78 | #2 TREATED WTR PP B REMOTE | D-DI | 24VDC | S | - | - | - | - | - | YES | NO | - | - | - | - | - | - | WASTEWATER RECYCLE AND DISCHARGE SYSTEM (COMMON) | RFW | TC0-1-KWM02-D6302 | - | MCC | DCDAS | - | - | -